## Minimum Melting Data
S&C Fault Tamer Fuse Limiter | [9 empty] | S&C Fault Tamer Fuse Limiter
S&C Standard Speed (TCC 123-8) | [9 empty] | S&C Standard Speed (TCC 123-8)
Minimum Melting Time-Current Characteristic Curve Dated September 29, 2003 | [9 empty] | Minimum Melting Time-Current Characteristic Curve Dated September 29, 2003
Tolerance in Terms of Current: Plus 10% withing coordinating range (melting times less than 10 seconds) | [9 empty] | Tolerance in Terms of Current: Plus 10% withing coordinating range (melting times less than 10 seconds)
1A |  | 2A |  | 3A |  | 5A |  | 7A |  | 10A |  | 15A |  | 20A
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
50.1664 | 0.01 | 93.0694 | 0.01 | 142.358 | 0.01 | 226.635 | 0.01 | 341.498 | 0.01 | 517.155 | 0.01 | 605 | 0.01 | 605 | 0.01
47.0564 | 0.011377 | 86.8642 | 0.011468 | 133.933 | 0.01132 | 207.129 | 0.012008 | 318.73 | 0.011503 | 467.006 | 0.012399 | 88.1861 | 0.51761 | 89.2894 | 0.5035
43.7874 | 0.013126 | 80.6683 | 0.013298 | 123.76 | 0.013298 | 190.251 | 0.014276 | 293.637 | 0.013621 | 424.683 | 0.014978 | 82.3569 | 0.6 | 84.004 | 0.5821
40.7863 | 0.015144 | 73.7991 | 0.015888 | 111.647 | 0.016438 | 172.491 | 0.017402 | 268.364 | 0.016307 | 386.968 | 0.018004 | 75.9626 | 0.71945 | 78.7408 | 0.7
37.915 | 0.017489 | 68.3982 | 0.018441 | 101.427 | 0.019877 | 156.232 | 0.021191 | 246.003 | 0.019484 | 352.251 | 0.021728 | 72.4937 | 0.8 | 74.7309 | 0.8
35.2458 | 0.020178 | 62.5112 | 0.0221 | 89.6888 | 0.025472 | 140.66 | 0.026195 | 225.731 | 0.023141 | 315.558 | 0.026859 | 69.0558 | 0.90365 | 71.8456 | 0.9
32.8301 | 0.023303 | 56.6191 | 0.026725 | 80.0255 | 0.031931 | 128.939 | 0.03105 | 203.842 | 0.028406 | 285.815 | 0.032838 | 65.0729 | 1.0471 | 69.2947 | 1
30.5494 | 0.026805 | 51.4879 | 0.032349 | 71.4749 | 0.040189 | 117.137 | 0.037547 | 180.61 | 0.036039 | 258.357 | 0.040149 | 56.3638 | 1.5276 | 62.3304 | 1.4488
28.3988 | 0.03105 | 46.2169 | 0.040028 | 62.7618 | 0.052174 | 106.521 | 0.045677 | 162.934 | 0.044549 | 235.649 | 0.048115 | 51.1446 | 2 | 58.0096 | 2
26.5053 | 0.035751 | 41.6519 | 0.049136 | 55.5535 | 0.066526 | 96.2882 | 0.055678 | 147.281 | 0.054576 | 212.585 | 0.05924 | 47.687 | 2.5 | 55.2586 | 2.5
24.5656 | 0.041454 | 37.9529 | 0.05924 | 50.62 | 0.080286 | 85.0591 | 0.071421 | 133.799 | 0.066128 | 191.396 | 0.072791 | 45.0194 | 3 | 53.9759 | 2.851
22.9277 | 0.047684 | 34.1699 | 0.072791 | 46.0785 | 0.096505 | 76.5042 | 0.08811 | 123.142 | 0.078382 | 172.491 | 0.0898 | 43.1917 | 3.5 | 52.2637 | 3.5
21.2923 | 0.055179 | 30.4884 | 0.091523 | 42.9633 | 0.1109 | 68.2615 | 0.11078 | 112.431 | 0.09384 | 157.487 | 0.1073 | 41.7446 | 4 | 51.3334 | 4
19.833 | 0.063662 | 27.6423 | 0.11145 | 39.7793 | 0.12949 | 61.8892 | 0.13464 | 101.529 | 0.11508 | 143.501 | 0.12923 | 39.8382 | 5 | 49.9689 | 5
18.4367 | 0.073596 | 24.3698 | 0.14382 | 36.9788 | 0.14984 | 55.6091 | 0.1676 | 90.9533 | 0.14397 | 130.626 | 0.15643 | 38.5745 | 6 | 49.0795 | 6
17.1903 | 0.08474 | 21.6357 | 0.18265 | 33.393 | 0.1843 | 50.4179 | 0.20369 | 82.876 | 0.1734 | 117.842 | 0.19106 | 37.4111 | 7 | 48.2836 | 7
15.9641 | 0.098061 | 19.324 | 0.22715 | 30.3667 | 0.22265 | 45.2113 | 0.2533 | 75.3652 | 0.20989 | 106.308 | 0.23383 | 36.61 | 8 | 47.687 | 8
14.8254 | 0.11359 | 17.4676 | 0.27688 | 27.8643 | 0.26443 | 40.8271 | 0.31156 | 69.5013 | 0.2473 | 97.1587 | 0.28135 | 35.9584 | 9 | 47.1737 | 9
13.713 | 0.1325 | 16.3356 | 0.31501 | 25.2631 | 0.32298 | 36.9419 | 0.37978 | 62.7618 | 0.3057 | 89.0632 | 0.33583 | 35.4487 | 10 | 46.6659 | 10
12.7859 | 0.15196 | 15.2008 | 0.36307 | 22.8819 | 0.39449 | 34.5479 | 0.43729 | 56.2804 | 0.38398 | 79.6264 | 0.42436 | 33.8922 | 15.3109 | 45.1856 | 15
11.8384 | 0.1769 | 14.0883 | 0.42267 | 20.829 | 0.47371 | 32.4385 | 0.49949 | 51.3336 | 0.46806 | 71.4034 | 0.53517 | 33.1665 | 20.6063 | 44.3813 | 20
10.9501 | 0.20697 | 13.0442 | 0.49403 | 18.7528 | 0.58792 | 30.2455 | 0.58265 | 47.8153 | 0.5449 | 64.3506 | 0.66954 | 32.7491 | 25.527 | 43.7421 | 25
10.2098 | 0.23831 | 12.2478 | 0.56318 | 17.1046 | 0.7074 | 28.2007 | 0.67695 | 44.672 | 0.63181 | 58.4602 | 0.82517 | 32.3445 | 30.4089 | 43.1917 | 30
9.406 | 0.28107 | 11.3742 | 0.65826 | 15.7895 | 0.82848 | 26.4524 | 0.78024 | 41.9025 | 0.72676 | 52.8441 | 1.0334 | 31.8787 | 40.3645 | 42.3545 | 41.6869
8.6915 | 0.32885 | 10.6904 | 0.7474 | 14.7515 | 0.95489 | 24.8125 | 0.90108 | 39.2655 | 0.83932 | 48.8301 | 1.2446 | 31.6519 | 49.6592 | 42.0436 | 50
7.9038 | 0.39213 | 10.0276 | 0.85799 | 13.7267 | 1.105 | 23.2975 | 1.0375 | 36.8681 | 0.96835 | 45.5744 | 1.4664 | 31.369 | 60.3949 | 41.6677 | 60
7.2525 | 0.46294 | 9.4437 | 0.97418 | 12.9144 | 1.2609 | 22.117 | 1.1675 | 34.6863 | 1.1161 | 43.3084 | 1.6634 | 31.2536 | 69.024 | 41.4477 | 70
6.6615 | 0.54708 | 8.876 | 1.1116 | 12.1017 | 1.4577 | 20.829 | 1.3349 | 32.6011 | 1.2902 | 41.1962 | 1.8924 | 31.1458 | 80 | 41.2952 | 80
6.1617 | 0.63816 | 8.2594 | 1.2928 | 11.4198 | 1.6331 | 19.8131 | 1.5051 | 30.7333 | 1.4886 | 39.3441 | 2.1273 | 31.0313 | 90 | 41.1529 | 90
5.7509 | 0.73333 | 7.8096 | 1.4591 | 10.8411 | 1.8578 | 18.7716 | 1.7174 | 29.3222 | 1.6717 | 37.8771 | 2.3463 | 30.9742 | 100 | 40.9261 | 100
5.3567 | 0.8503 | 7.4734 | 1.611 | 10.3537 | 2.0512 | 17.9098 | 1.9384 | 28.2289 | 1.8457 | 36.138 | 2.6561 | 30 | 300 | 40 | 300
5.0146 | 0.97808 | 7.1804 | 1.7697 | 9.9677 | 2.2856 | 17.0193 | 2.2008 | 27.0408 | 2.0623 | 34.617 | 2.9827
4.732 | 1.1161 | 6.8713 | 1.9696 | 9.7163 | 2.4099 | 16.3029 | 2.4617 | 25.9805 | 2.2792 | 33.4264 | 3.2866
4.4564 | 1.2864 | 6.5624 | 2.2386 | 9.3685 | 2.6669 | 15.648 | 2.726 | 24.8125 | 2.5673 | 32.471 | 3.571
4.2095 | 1.4723 | 6.415 | 2.3988 | 9.0916 | 2.9309 | 15.1704 | 2.959 | 23.7206 | 2.8888 | 31.4169 | 3.9505
3.9765 | 1.7072 | 6.1248 | 2.8184 | 8.8671 | 3.155 | 14.7958 | 3.1514 | 22.6996 | 3.2539 | 30.2757 | 4.4099
3.761 | 1.9676 | 5.9061 | 3.2997 | 8.6298 | 3.4914 | 14.3442 | 3.4551 | 21.8532 | 3.5997 | 29.2636 | 4.9128
3.5571 | 2.2724 | 5.7491 | 3.7428 | 8.3674 | 3.9174 | 13.9063 | 3.8223 | 20.9963 | 4.0303 | 28.1443 | 5.5781
3.3947 | 2.6218 | 5.586 | 4.3312 | 8.1171 | 4.5394 | 13.5494 | 4.1864 | 20.2336 | 4.5125 | 27.2035 | 6.2956
3.2456 | 3.0067 | 5.4463 | 4.9523 | 7.775 | 5.668 | 13.2281 | 4.6036 | 19.382 | 5.1492 | 26.2154 | 7.1911
3.1769 | 3.2885 | 5.3015 | 5.7825 | 7.5683 | 6.6449 | 12.85 | 5.201 | 18.4921 | 5.9646 | 25.3644 | 8.0917
3.0754 | 3.7056 | 5.1606 | 6.7385 | 7.3943 | 7.79 | 12.5202 | 5.8524 | 17.7848 | 6.8131 | 24.6887 | 8.9696
3.0047 | 4.1365 | 5.0781 | 7.7357 | 7.2227 | 9.0961 | 12.2233 | 6.6648 | 17.2247 | 7.5977 | 24.2159 | 9.9428
2.9404 | 4.6452 | 4.9694 | 8.9966 | 7.1072 | 10.2329 | 11.9813 | 7.3879 | 16.8499 | 8.2717 | 23.6537 | 11.1322
2.8721 | 5.2585 | 4.8899 | 10.3588 | 6.9422 | 12.3595 | 11.7206 | 8.3884 | 16.4833 | 9.1052 | 23.11 | 12.5892
2.8158 | 5.821 | 4.8029 | 12.0353 | 6.8061 | 15.0314 | 11.4885 | 9.6296 | 16.1569 | 9.9826 | 22.6152 | 14.6266
2.7265 | 6.8391 | 4.7174 | 14.337 | 6.6252 | 19.2752 | 11.261 | 11.0435 | 15.9004 | 10.9665 | 22.2126 | 16.6406
2.6632 | 7.8605 | 4.6334 | 16.9428 | 6.5073 | 23.2274 | 11.049 | 12.7667 | 15.57 | 12.5264 | 21.7771 | 19.6847
2.6068 | 8.9966 | 4.5593 | 20.7562 | 6.3915 | 28.987 | 10.8628 | 14.7294 | 15.3229 | 14.166 | 21.4684 | 23.0541
2.5739 | 9.8401 | 4.4854 | 25.527 | 6.3343 | 33.0442 | 10.7118 | 17.0789 | 15.0947 | 16.0682 | 21.1982 | 27.4632
2.5235 | 11.5634 | 4.43 | 30.0796 | 6.2799 | 38.1241 | 10.6121 | 19.6062 | 14.8551 | 18.4829 | 20.9315 | 32.7481
2.47 | 13.6105 | 4.3823 | 35.1578 | 6.2174 | 43.7218 | 10.5172 | 22.6202 | 14.634 | 21.0278 | 20.7444 | 39.0502
2.4344 | 15.6715 | 4.3431 | 40.9703 | 6.174 | 49.9413 | 10.404 | 26.0716 | 14.4594 | 24.5778 | 20.5589 | 47.696
2.3911 | 18.3654 | 4.3043 | 48.6109 | 6.1433 | 57.8497 | 10.3467 | 30.1097 | 14.3012 | 28.5268 | 20.361 | 59.9103
2.361 | 21.3029 | 4.2658 | 59.2549 | 6.1221 | 67.2118 | 10.292 | 34.8428 | 14.1731 | 33.6444 | 20.2539 | 72.0852
2.3318 | 24.4553 | 4.2277 | 70.6578 | 6.0884 | 78.8738 | 10.2542 | 40.1992 | 14.0742 | 39.0892 | 20.2336 | 90.0036
2.3025 | 29.1322 | 4.1899 | 84.7622 | 6.0674 | 93.2095 | 10.2353 | 46.5649 | 14.004 | 46.5184 | 20.173 | 111.146
2.2699 | 34.2555 | 4.1524 | 99.3116 | 6.0562 | 112.488 | 10.2 | 54.2633 | 13.9481 | 55.9159 | 20.1327 | 139.889
2.2496 | 39.7594 | 4.1153 | 126.4736 | 6.0562 | 131.874 | 10.1625 | 64.3829 | 13.9063 | 67.2118 | 20.0724 | 172.751
2.2254 | 46.1318 | 4.0851 | 147.65 | 6.0451 | 157.409 | 10.1438 | 77.933 | 13.8924 | 80.0658 | 20.0123 | 215.2782
2.2014 | 53.1888 | 4.0635 | 172.405 | 6.0242 | 194.776 | 10.1274 | 92.8374 | 13.9063 | 95.7604 | 20.0493 | 243.922
2.1817 | 61.3655 | 4.042 | 205.172 | 6.0242 | 238.376 | 10.1088 | 111.146 | 13.8924 | 120.644 | 20.0124 | 275.572
2.1543 | 75.4031 | 4.0272 | 249.348 | 6.0131 | 268.232 | 10.0716 | 139.33 | 13.8924 | 148.242 | 20.0124 | 301.524
2.1389 | 88.1332 | 4.0059 | 298.226 | 6.0021 | 297.928 | 10.0531 | 172.233 | 13.8924 | 190.157
2.1198 | 102.498 |  |  |  |  | 10.0369 | 211.844 | 13.9063 | 226.977
2.097 | 122.223 |  |  |  |  | 10.0184 | 249.598 | 13.8924 | 259.784
2.0821 | 142.715 |  |  |  |  | 10 | 299.721 | 13.8924 | 300.321
2.0635 | 168.991
2.045 | 195.8845
2.0305 | 226.524
2.0156 | 259.524
2.0012 | 301.223