## 153_1
S&C Power Fuses - Types SMD-1A, -2B, - 2C, -3, and -50 | [9 empty] | S&C Power Fuses - Types SMD-1A, -2B, - 2C, -3, and -50 | [9 empty] | S&C Power Fuses - Types SMD-1A, -2B, - 2C, -3, and -50 | [9 empty] | S&C Power Fuses - Types SMD-1A, -2B, - 2C, -3, and -50
Standard Speed (TCC 153-1) | [9 empty] | Standard Speed (TCC 153-1) | [9 empty] | Standard Speed (TCC 153-1) | [9 empty] | Standard Speed (TCC 153-1)
Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988
Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 10E thru 300E | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 10E thru 300E | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 10E thru 300E | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 10E thru 300E
|  |  | Plus 15% for fuse units rated 5E thru 7E | [9 empty] | Plus 15% for fuse units rated 5E thru 7E | [9 empty] | Plus 15% for fuse units rated 5E thru 7E | [9 empty] | Plus 15% for fuse units rated 5E thru 7E
|  |  | Plus 20% for fuse units rated 3E | [9 empty] | Plus 20% for fuse units rated 3E | [9 empty] | Plus 20% for fuse units rated 3E | [9 empty] | Plus 20% for fuse units rated 3E
3E |  | 5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 2-200E |  | 2-250E |  | 2-300E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
79.2759 | 0.01 | 260.065 | 0.01 | 373.879 | 0.01 | 507.721 | 0.01 | 656.505 | 0.01 | 751.395 | 0.01 | 1034.76 | 0.01 | 1326.01 | 0.01 | 1462.54 | 0.01 | 1877.93 | 0.01 | 2289.13 | 0.01 | 3133.57 | 0.01 | 3967.65 | 0.01 | 4929.18 | 0.01 | 6335.53 | 0.01 | 7722.77 | 0.01 | 8586.34 | 0.01 | 9517.88 | 0.01 | 11671.7 | 0.01 | 14763.7 | 0.01 | 17050.3 | 0.01 | 20971.6 | 0.01 | 26820.6 | 0.01
77.4733 | 0.010492 | 255.937 | 0.010367 | 365.378 | 0.01046 | 495.68 | 0.010439 | 647.378 | 0.010274 | 740.208 | 0.010346 | 1010.22 | 0.010544 | 1295.86 | 0.01045 | 1436.45 | 0.010377 | 1849.98 | 0.010325 | 2261.83 | 0.010284 | 3090.01 | 0.010336 | 3916.4 | 0.010325 | 4855.8 | 0.010377 | 4522.99 | 0.019601 | 5409.59 | 0.020421 | 6044.65 | 0.020117 | 6633.77 | 0.020421 | 8332.58 | 0.01964 | 9985.88 | 0.02199 | 12707.2 | 0.018112 | 15660.9 | 0.017878 | 19968.8 | 0.01795
74.2126 | 0.011423 | 247.381 | 0.011085 | 350.7 | 0.0114 | 479.11 | 0.011196 | 623.24 | 0.011041 | 716.18 | 0.010997 | 978.412 | 0.011196 | 1222.83 | 0.011747 | 1396.78 | 0.010964 | 1798.89 | 0.01092 | 2208.19 | 0.010811 | 2980.74 | 0.011041 | 3800.65 | 0.010942 | 4731.17 | 0.010931 | 3203.27 | 0.039079 | 3770.37 | 0.041997 | 4442.3 | 0.03721 | 4660.73 | 0.041371 | 5807.63 | 0.040512 | 7397.73 | 0.039988 | 9807.75 | 0.030526 | 12087.5 | 0.030162 | 15629.6 | 0.029359
69.9607 | 0.012866 | 239.112 | 0.011936 | 331.601 | 0.012687 | 462.632 | 0.011984 | 604.82 | 0.01177 | 687.41 | 0.01202 | 947.598 | 0.011948 | 1151.62 | 0.013271 | 1343.36 | 0.011829 | 1724.91 | 0.011829 | 2138.65 | 0.011514 | 2875.35 | 0.011889 | 3543.71 | 0.012599 | 4573.02 | 0.011688 | 2208.19 | 0.082154 | 2699.79 | 0.081989 | 3174.57 | 0.073009 | 3245.19 | 0.084995 | 3892.97 | 0.0898 | 5830.91 | 0.064495 | 7164.75 | 0.056917 | 9227.36 | 0.0515 | 12656.5 | 0.044727
66.2168 | 0.014362 | 228.819 | 0.013008 | 313.228 | 0.014205 | 446.72 | 0.012866 | 583.434 | 0.012586 | 654.539 | 0.013284 | 907.715 | 0.013034 | 1053.56 | 0.015841 | 1277.84 | 0.0131 | 1649.01 | 0.012956 | 2060.96 | 0.012386 | 2762.6 | 0.012827 | 3258.19 | 0.014903 | 4354.34 | 0.012879 | 1496.56 | 0.17904 | 1952.62 | 0.15643 | 2365.93 | 0.13131 | 2356.49 | 0.16119 | 2815.59 | 0.17184 | 4651.42 | 0.10135 | 5596.68 | 0.093372 | 7316.8 | 0.082154 | 10218.2 | 0.068278
61.8637 | 0.016421 | 215.278 | 0.014711 | 292.344 | 0.01634 | 411.55 | 0.015144 | 557.204 | 0.013785 | 613.347 | 0.015098 | 859.139 | 0.014506 | 980.371 | 0.018276 | 1197.42 | 0.014933 | 1559.2 | 0.014463 | 1984.11 | 0.013378 | 2659.59 | 0.013868 | 3025.79 | 0.017194 | 4141.98 | 0.014248 | 1060.96 | 0.35517 | 1450.88 | 0.28304 | 1868.57 | 0.2101 | 1853.68 | 0.26285 | 2034.34 | 0.33482 | 3449.31 | 0.18541 | 4341.3 | 0.15518 | 5860.14 | 0.1282 | 8282.73 | 0.10361
57.279 | 0.019155 | 204.574 | 0.016274 | 260.065 | 0.020709 | 380.289 | 0.017754 | 527.913 | 0.015373 | 560.557 | 0.018148 | 813.976 | 0.016193 | 897.785 | 0.021641 | 1120.94 | 0.017023 | 1453.79 | 0.016686 | 1893.02 | 0.014652 | 2464.95 | 0.016112 | 2787.58 | 0.020299 | 3789.27 | 0.017023 | 850.591 | 0.55313 | 1124.31 | 0.47276 | 1419.31 | 0.3638 | 1477.24 | 0.4143 | 1606.68 | 0.54599 | 2732.38 | 0.29607 | 3397.95 | 0.25381 | 4702.87 | 0.19906 | 6720.57 | 0.15753
53.46 | 0.022056 | 190.744 | 0.018664 | 233.441 | 0.025702 | 351.051 | 0.020792 | 499.662 | 0.01716 | 521.094 | 0.021001 | 765.808 | 0.018221 | 829.589 | 0.02532 | 1042.03 | 0.01968 | 1298.45 | 0.020792 | 1781 | 0.01657 | 2296.01 | 0.018571 | 2542.56 | 0.024376 | 3536.63 | 0.019503 | 724.101 | 0.76632 | 921.434 | 0.7074 | 1224.06 | 0.49452 | 1217.95 | 0.6193 | 1388.43 | 0.7474 | 2284.56 | 0.42906 | 2779.23 | 0.37864 | 3677.28 | 0.32525 | 5635.99 | 0.22421
49.3992 | 0.025677 | 178.383 | 0.02134 | 206.424 | 0.032871 | 319.556 | 0.025093 | 461.246 | 0.020077 | 487.325 | 0.024013 | 713.321 | 0.021022 | 768.877 | 0.029417 | 962.882 | 0.023048 | 1185.51 | 0.024968 | 1685.69 | 0.018441 | 2125.85 | 0.021641 | 2365.93 | 0.028039 | 3261.45 | 0.02291 | 625.738 | 1.05 | 761.226 | 1.0649 | 1060.96 | 0.66554 | 1045.16 | 0.86229 | 1211.88 | 1.0079 | 1960.45 | 0.59146 | 2266.35 | 0.57283 | 2971.82 | 0.4985 | 4731.17 | 0.31849
44.6982 | 0.031299 | 165.493 | 0.024843 | 184.552 | 0.041001 | 289.146 | 0.030618 | 428.775 | 0.023303 | 448.062 | 0.028321 | 662.441 | 0.0244 | 709.053 | 0.034625 | 898.683 | 0.026432 | 1089.99 | 0.029506 | 1576.44 | 0.021064 | 1915.87 | 0.026485 | 2221.48 | 0.031868 | 3034.88 | 0.026406 | 562.241 | 1.3402 | 667.094 | 1.4302 | 930.694 | 0.87971 | 923.278 | 1.1443 | 1099.85 | 1.271 | 1694.14 | 0.81452 | 1912.04 | 0.826 | 2622.62 | 0.65171 | 4043.75 | 0.43641
40.7287 | 0.03766 | 153.382 | 0.028893 | 162.866 | 0.052488 | 262.941 | 0.037099 | 400.187 | 0.026725 | 406.641 | 0.034315 | 613.347 | 0.028434 | 644.15 | 0.041955 | 822.979 | 0.031519 | 1010.22 | 0.034384 | 1496.56 | 0.023443 | 1752.73 | 0.031677 | 2083.76 | 0.036219 | 2743.33 | 0.032414 | 512.823 | 1.675 | 604.82 | 1.8164 | 837.089 | 1.1251 | 837.927 | 1.4504 | 1004.18 | 1.5965 | 1510.09 | 1.0638 | 1660.59 | 1.1364 | 2363.57 | 0.82435 | 3438.97 | 0.61375
37.7103 | 0.04393 | 139.76 | 0.034799 | 147.958 | 0.063598 | 240.07 | 0.04446 | 362.466 | 0.032446 | 362.829 | 0.04306 | 577.051 | 0.032156 | 596.412 | 0.048744 | 755.161 | 0.037472 | 926.979 | 0.040796 | 1393.99 | 0.026939 | 1573.3 | 0.039197 | 1942.88 | 0.041454 | 2509.72 | 0.03869 | 470.093 | 2.0789 | 557.204 | 2.2724 | 757.43 | 1.4388 | 764.277 | 1.831 | 925.127 | 1.9716 | 1359.57 | 1.3673 | 1477.24 | 1.5006 | 2125.85 | 1.0595 | 3031.85 | 0.81127
34.6721 | 0.05207 | 128.243 | 0.041247 | 132.017 | 0.079885 | 218.969 | 0.053442 | 332.597 | 0.038613 | 321.8 | 0.054412 | 541.819 | 0.036255 | 551.108 | 0.056974 | 685.351 | 0.045403 | 848.043 | 0.048696 | 1328.66 | 0.029654 | 1417.89 | 0.048308 | 1786.35 | 0.049136 | 2246.05 | 0.048019 | 433.517 | 2.5931 | 509.755 | 2.9887 | 693.625 | 1.7965 | 704.812 | 2.2861 | 866.04 | 2.3818 | 1236.36 | 1.7399 | 1331.32 | 1.9874 | 1910.13 | 1.3852 | 2770.9 | 0.99485
31.3726 | 0.063535 | 113.401 | 0.052963 | 121.138 | 0.094783 | 199.923 | 0.064109 | 300.645 | 0.047162 | 286.842 | 0.068552 | 501.664 | 0.042081 | 491.731 | 0.071492 | 624.487 | 0.054794 | 778.938 | 0.057661 | 1265.13 | 0.032805 | 1298.45 | 0.057546 | 1632.6 | 0.058533 | 2067.15 | 0.056917 | 402.595 | 3.2474 | 472.922 | 3.8878 | 646.085 | 2.1768 | 658.478 | 2.8062 | 818.875 | 2.8316 | 1136.75 | 2.1877 | 1221.61 | 2.5468 | 1754.48 | 1.7295 | 2557.86 | 1.2151
28.9316 | 0.074708 | 100.779 | 0.066993 | 107.332 | 0.1211 | 183.265 | 0.076065 | 269.328 | 0.058768 | 257.477 | 0.08491 | 452.113 | 0.051759 | 449.408 | 0.085849 | 583.434 | 0.062652 | 708.345 | 0.069588 | 1202.22 | 0.036255 | 1190.26 | 0.068758 | 1519.18 | 0.067599 | 1861.11 | 0.069937 | 376.882 | 4.0142 | 446.72 | 4.8688 | 607.852 | 2.5931 | 608.46 | 3.6945 | 767.341 | 3.5143 | 1055.67 | 2.707 | 1120.94 | 3.2931 | 1590.7 | 2.2884 | 2316.77 | 1.554
26.5209 | 0.088818 | 89.8313 | 0.084233 | 94.4371 | 0.15612 | 169.174 | 0.089442 | 243.942 | 0.071707 | 228.59 | 0.10719 | 418.606 | 0.060315 | 412.787 | 0.10115 | 545.625 | 0.071564 | 648.026 | 0.082896 | 1127.69 | 0.041165 | 1087.82 | 0.082154 | 1423.58 | 0.076906 | 1709.45 | 0.082648 | 354.225 | 5.1082 | 426.21 | 6.1709 | 572.453 | 3.1263 | 570.738 | 4.7343 | 729.188 | 4.2667 | 984.3 | 3.3563 | 1053.56 | 4.0465 | 1480.19 | 2.9062 | 2104.7 | 2.0014
24.0452 | 0.10794 | 80.5545 | 0.10433 | 85.1091 | 0.19221 | 156.324 | 0.10423 | 223.393 | 0.085421 | 209.543 | 0.12769 | 379.15 | 0.07367 | 382.96 | 0.11764 | 498.165 | 0.085935 | 584.018 | 0.10206 | 1073.77 | 0.045403 | 994.192 | 0.098651 | 1295.86 | 0.092628 | 1563.88 | 0.098651 | 330.938 | 7.2489 | 408.271 | 8.116 | 543.446 | 3.7541 | 543.99 | 6.0973 | 696.405 | 5.2062 | 923.278 | 4.1906 | 1002.17 | 5.0675 | 1366.39 | 3.9229 | 1952.62 | 2.5039
22.4196 | 0.12466 | 72.7431 | 0.12756 | 76.6258 | 0.2376 | 142.584 | 0.12554 | 205.6 | 0.10044 | 192.276 | 0.15211 | 349.649 | 0.086366 | 355.289 | 0.13654 | 466.348 | 0.097865 | 530.559 | 0.12367 | 1016.3 | 0.050734 | 866.04 | 0.12936 | 1196.23 | 0.10848 | 1435.01 | 0.11717 | 313.228 | 10.5999 | 393.048 | 10.9445 | 520.053 | 4.4231 | 518.495 | 8.1649 | 669.098 | 6.5394 | 872.123 | 5.2954 | 953.301 | 6.5328 | 1270.2 | 5.3486 | 1797.1 | 3.2539
20.5104 | 0.1494 | 62.7987 | 0.17116 | 68.644 | 0.29577 | 132.546 | 0.14541 | 188.28 | 0.11965 | 177.848 | 0.17761 | 320.836 | 0.10227 | 322.445 | 0.16511 | 430.493 | 0.11496 | 485.38 | 0.14761 | 954.255 | 0.057777 | 789.13 | 0.15612 | 1102.05 | 0.1268 | 1295.86 | 0.14382 | 299.445 | 16.1973 | 378.392 | 15.829 | 494.69 | 5.4403 | 501.664 | 10.7601 | 642.863 | 8.4388 | 831.25 | 6.6782 | 916.838 | 8.4388 | 1196.23 | 7.1124 | 1690.75 | 4.0586
18.8579 | 0.17779 | 53.8894 | 0.23266 | 60.9427 | 0.37525 | 122.478 | 0.17031 | 171.56 | 0.14483 | 157.58 | 0.22556 | 294.692 | 0.12122 | 303.363 | 0.1869 | 397.395 | 0.13504 | 441.391 | 0.17797 | 901.384 | 0.064689 | 719.769 | 0.18784 | 998.177 | 0.15394 | 1183.14 | 0.17271 | 289.435 | 25.8121 | 366.475 | 23.0081 | 475.293 | 6.6915 | 484.41 | 14.8625 | 621.994 | 11.1211 | 785.98 | 9.2613 | 892.415 | 10.6636 | 1134.48 | 9.6008 | 1598.67 | 5.0624
17.0122 | 0.21911 | 48.0352 | 0.29254 | 54.7586 | 0.46387 | 112.723 | 0.20006 | 152.922 | 0.18211 | 139.481 | 0.28934 | 270.408 | 0.14368 | 282.571 | 0.21477 | 367.944 | 0.15721 | 402.193 | 0.21413 | 820.514 | 0.077913 | 663.103 | 0.22132 | 888.852 | 0.19395 | 1089.99 | 0.2043 | 281.443 | 42.8132 | 355.644 | 37.7448 | 457.571 | 8.247 | 469.623 | 21.9517 | 599.401 | 15.6558 | 752.899 | 12.8821 | 863.446 | 14.5682 | 1098.75 | 12.0835 | 1502.56 | 6.6183
15.6886 | 0.25972 | 43.6819 | 0.35304 | 48.276 | 0.59681 | 105.102 | 0.23012 | 136.583 | 0.22828 | 127.604 | 0.34502 | 248.87 | 0.16912 | 260.325 | 0.25179 | 340.676 | 0.18339 | 354.579 | 0.27578 | 764.277 | 0.089442 | 618.892 | 0.25356 | 805.877 | 0.23571 | 1026.52 | 0.23058 | 276.976 | 72.6642 | 346.863 | 62.1685 | 444.492 | 10.3588 | 458.028 | 34.8428 | 582.851 | 22.0177 | 722.654 | 18.5384 | 836.253 | 20.632 | 1073.77 | 15.1628 | 1430.71 | 8.3632
14.7307 | 0.29785 | 40.2429 | 0.41472 | 43.5946 | 0.73186 | 97.1187 | 0.26816 | 126.208 | 0.26629 | 115.692 | 0.42183 | 223.616 | 0.20905 | 238.157 | 0.30054 | 319.236 | 0.20926 | 329.947 | 0.31977 | 716.896 | 0.10155 | 583.434 | 0.28589 | 723.377 | 0.29108 | 968.677 | 0.26076 | 275.319 | 129.134 | 338.638 | 107.002 | 430.924 | 13.6378 | 450.758 | 54.1549 | 570.738 | 31.2446 | 701.998 | 25.6321 | 813.162 | 30.9337 | 1056.72 | 19.7636 | 1388.43 | 10.0126
13.8728 | 0.33988 | 37.635 | 0.47513 | 39.3279 | 0.8939 | 89.8313 | 0.31344 | 118.384 | 0.30175 | 109.063 | 0.47182 | 198.131 | 0.26443 | 219.627 | 0.35304 | 294.398 | 0.24557 | 306.719 | 0.36893 | 659.796 | 0.12013 | 542.903 | 0.33016 | 661.779 | 0.34571 | 914.092 | 0.29489 | 274.494 | 262.133 | 332.264 | 169.839 | 417.77 | 18.781 | 444.047 | 93.4895 | 562.804 | 45.8258 | 686.037 | 37.1828 | 798.656 | 49.6425 | 1032.69 | 28.243 | 1348.74 | 12.2661
13.0649 | 0.39095 | 35.5143 | 0.53197 | 36.5227 | 1.0406 | 82.4287 | 0.37152 | 112.048 | 0.33482 | 102.712 | 0.52615 | 179.995 | 0.32073 | 193.24 | 0.45241 | 275.595 | 0.28079 | 291.468 | 0.41018 | 606.637 | 0.14197 | 510.776 | 0.37077 | 623.863 | 0.38939 | 866.04 | 0.33182 | 274.769 | 605.984 | 329.617 | 314.773 | 409.498 | 25.8897 | 439.629 | 174.312 | 555.535 | 76.161 | 673.125 | 55.1385 | 791.501 | 77.5443 | 1015.29 | 40.3603 | 1316.76 | 15.6715
12.3411 | 0.44702 | 33.513 | 0.59562 | 34.3271 | 1.178 | 75.9393 | 0.43641 | 106.371 | 0.37152 | 97.0216 | 0.58969 | 159.801 | 0.4065 | 174.85 | 0.55202 | 249.368 | 0.34295 | 277.808 | 0.45196 | 525.28 | 0.18878 | 482.959 | 0.41347 | 591.068 | 0.42949 | 801.056 | 0.39056 | 274.769 | 605.984 | 328.63 | 602.961 | 399.787 | 41.0934 | 440.509 | 362.437 | 550.007 | 150.182 | 662.441 | 83.5002 | 788.341 | 126.957 | 1002.17 | 64.641 | 1291.97 | 20.8811
11.8453 | 0.49551 | 31.1849 | 0.68787 | 32.4576 | 1.3269 | 71.4454 | 0.49403 | 100.981 | 0.41306 | 89.4727 | 0.69201 | 142.869 | 0.50958 | 159.641 | 0.65892 | 230.657 | 0.40165 | 267.45 | 0.49009 | 458.487 | 0.24804 | 463.095 | 0.45106 | 560.557 | 0.47847 | 756.673 | 0.4408 | 274.769 | 605.984 | 328.63 | 602.961 | 391.87 | 66.6762 | 440.509 | 610.241 | 549.457 | 267.963 | 658.478 | 141.436 | 788.341 | 220.71 | 992.206 | 102.806 | 1258.82 | 29.249
11.2564 | 0.56543 | 29.1057 | 0.78808 | 31.2786 | 1.436 | 68.029 | 0.54817 | 95.1956 | 0.46294 | 84.3465 | 0.7818 | 130.312 | 0.61008 | 146.926 | 0.77402 | 210.173 | 0.4828 | 252.884 | 0.54872 | 415.686 | 0.30145 | 445.381 | 0.49058 | 534.286 | 0.52826 | 713.321 | 0.5025 | 274.769 | 605.984 | 328.63 | 602.961 | 385.65 | 112.826 | 440.509 | 610.241 | 550.557 | 449.373 | 658.478 | 212.906 | 789.13 | 378.362 | 988.245 | 174.836 | 1231.42 | 41.0113
10.6646 | 0.65301 | 27.5206 | 0.88236 | 29.9921 | 1.5712 | 63.4298 | 0.62929 | 90.5529 | 0.51111 | 78.1737 | 0.91014 | 117.44 | 0.75415 | 137.13 | 0.88767 | 192.276 | 0.57398 | 242.968 | 0.5974 | 372.386 | 0.37638 | 427.918 | 0.53091 | 501.664 | 0.6016 | 673.125 | 0.57055 | 274.769 | 605.984 | 328.63 | 602.961 | 380.289 | 218.514 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 374.972 | 789.13 | 522.097 | 987.257 | 322.419 | 1213.09 | 63.6786
9.9835 | 0.78024 | 25.7886 | 1.0038 | 28.9027 | 1.7038 | 59.8555 | 0.70881 | 85.2795 | 0.57686 | 74.5846 | 1.0058 | 109.282 | 0.8727 | 128.115 | 1.0252 | 171.56 | 0.72169 | 234.377 | 0.64522 | 347.21 | 0.43424 | 400.587 | 0.60947 | 473.869 | 0.67898 | 638.378 | 0.64072 | 274.769 | 605.984 | 328.63 | 602.961 | 380.289 | 393.017 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1198.62 | 97.8905
9.5061 | 0.90289 | 23.6872 | 1.1863 | 27.7972 | 1.8661 | 56.7658 | 0.7865 | 78.4871 | 0.68102 | 70.5226 | 1.1307 | 102.609 | 0.99485 | 119.454 | 1.1816 | 157.737 | 0.86316 | 224.512 | 0.70669 | 328.63 | 0.4828 | 379.909 | 0.68512 | 445.827 | 0.77479 | 609.069 | 0.71166 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1195.03 | 164.161
9.0969 | 1.0375 | 22.0858 | 1.3659 | 26.8411 | 2.0195 | 53.46 | 0.8948 | 72.6704 | 0.79441 | 66.6819 | 1.2736 | 96.6343 | 1.1228 | 111.936 | 1.3551 | 148.998 | 0.9732 | 213.349 | 0.78808 | 312.602 | 0.53357 | 354.225 | 0.79919 | 419.444 | 0.88501 | 569.598 | 0.82848 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1191.45 | 279.458
8.7315 | 1.191 | 20.7788 | 1.5416 | 25.8403 | 2.203 | 51.0566 | 0.98989 | 67.8252 | 0.91561 | 63.8754 | 1.4033 | 92.3821 | 1.2397 | 106.264 | 1.5187 | 139.9 | 1.1172 | 201.327 | 0.89748 | 300.345 | 0.58091 | 334.264 | 0.90923 | 399.387 | 0.98594 | 543.446 | 0.92389 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
8.4312 | 1.3442 | 19.7259 | 1.7106 | 25.0265 | 2.3841 | 48.9077 | 1.0875 | 63.5568 | 1.0479 | 60.6994 | 1.5743 | 87.7888 | 1.3852 | 99.9763 | 1.7504 | 132.149 | 1.2685 | 189.413 | 1.0293 | 285.697 | 0.64522 | 316.06 | 1.0293 | 385.65 | 1.0713 | 510.776 | 1.0723 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
8.1738 | 1.5066 | 18.8014 | 1.8905 | 24.0692 | 2.6113 | 46.99 | 1.1851 | 59.6166 | 1.1982 | 57.6237 | 1.7786 | 84.5154 | 1.5036 | 95.1956 | 1.9539 | 124.578 | 1.4548 | 180.536 | 1.1478 | 270.949 | 0.71953 | 297.654 | 1.178 | 370.9 | 1.1792 | 482.476 | 1.2298 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
7.8376 | 1.7627 | 18.0642 | 2.0623 | 23.0792 | 2.9004 | 45.1926 | 1.2928 | 56.5392 | 1.3416 | 54.978 | 1.9854 | 81.0393 | 1.6584 | 90.0112 | 2.2341 | 118.858 | 1.6223 | 173.111 | 1.2622 | 258.251 | 0.796 | 282.007 | 1.3376 | 359.219 | 1.266 | 458.487 | 1.3949 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
7.6136 | 1.9775 | 17.2866 | 2.2724 | 22.1965 | 3.1862 | 43.2905 | 1.4231 | 53.5135 | 1.5141 | 52.5063 | 2.2296 | 77.7839 | 1.8218 | 84.8541 | 2.5724 | 113.174 | 1.8255 | 166.489 | 1.3935 | 244.43 | 0.89569 | 269.598 | 1.4856 | 347.558 | 1.3687 | 441.833 | 1.5278 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
7.4108 | 2.2386 | 16.6421 | 2.4814 | 21.4116 | 3.4968 | 41.0148 | 1.5934 | 50.7511 | 1.7004 | 50.1959 | 2.5039 | 73.9163 | 2.0582 | 81.6902 | 2.8316 | 107.978 | 2.0623 | 160.281 | 1.5263 | 233.441 | 0.9889 | 256.706 | 1.6885 | 333.93 | 1.5141 | 429.633 | 1.6468 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
7.264 | 2.4914 | 15.9735 | 2.7369 | 20.7373 | 3.8184 | 39.3672 | 1.7592 | 48.3243 | 1.8962 | 47.9872 | 2.8203 | 70.4522 | 2.3206 | 77.3959 | 3.2539 | 102.815 | 2.3463 | 155.389 | 1.6567 | 222.501 | 1.0973 | 246.148 | 1.8754 | 322.445 | 1.66 | 414.856 | 1.8164 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
7.0918 | 2.8543 | 15.4241 | 2.9857 | 20.1445 | 4.1282 | 37.4847 | 1.9618 | 45.8756 | 2.1294 | 46.2441 | 3.1419 | 67.1503 | 2.6061 | 73.4007 | 3.7691 | 98.2911 | 2.6349 | 150.194 | 1.8073 | 211.649 | 1.2286 | 239.351 | 2.0255 | 311.043 | 1.82 | 399.787 | 2.0074 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.9375 | 3.2539 | 14.9234 | 3.2409 | 19.2004 | 4.7343 | 35.7637 | 2.1877 | 43.5946 | 2.4009 | 44.2535 | 3.5817 | 64.5819 | 2.8888 | 69.4033 | 4.4187 | 94.2484 | 2.9708 | 145.901 | 1.9422 | 203.35 | 1.3578 | 231.581 | 2.2185 | 300.645 | 1.9914 | 382.96 | 2.2633 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.7797 | 3.8146 | 14.3814 | 3.5638 | 18.5958 | 5.2218 | 34.3614 | 2.4033 | 41.2204 | 2.7479 | 42.7314 | 4.0182 | 62.1117 | 3.2118 | 66.9492 | 4.9424 | 90.7341 | 3.3262 | 141.165 | 2.1337 | 193.433 | 1.5293 | 224.512 | 2.4421 | 289.435 | 2.2141 | 370.158 | 2.4964 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.6788 | 4.3182 | 13.8313 | 3.9505 | 18.0642 | 5.725 | 32.6529 | 2.7124 | 39.6042 | 3.0613 | 41.2617 | 4.526 | 59.26 | 3.6687 | 64.5819 | 5.5392 | 87.4383 | 3.7279 | 136.719 | 2.3299 | 186.034 | 1.6851 | 218.095 | 2.6614 | 277.253 | 2.4989 | 358.143 | 2.7562 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.5597 | 4.9721 | 13.3289 | 4.3791 | 17.6006 | 6.2142 | 31.4983 | 2.956 | 38.0132 | 3.3934 | 39.8027 | 5.1235 | 57.2217 | 4.0424 | 62.2983 | 6.2641 | 84.7693 | 4.1614 | 131.621 | 2.5905 | 178.919 | 1.8605 | 210.594 | 2.9442 | 269.059 | 2.7534 | 345.479 | 3.0644 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.4684 | 5.7365 | 12.9608 | 4.7486 | 17.1318 | 6.8267 | 30.4758 | 3.2054 | 36.4862 | 3.7842 | 38.3185 | 5.8524 | 55.4196 | 4.4586 | 60.3363 | 7.0628 | 82.3463 | 4.6499 | 126.967 | 2.9004 | 172.592 | 2.05 | 204.165 | 3.2441 | 258.509 | 3.1107 | 335.268 | 3.3731 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.3722 | 6.6051 | 12.5652 | 5.2427 | 16.759 | 7.3953 | 29.6047 | 3.4447 | 35.0205 | 4.2242 | 37.0747 | 6.6382 | 53.46 | 5.002 | 58.6703 | 7.9236 | 80.1527 | 5.2218 | 122.111 | 3.2734 | 165.163 | 2.316 | 196.749 | 3.6105 | 252.379 | 3.4104 | 326.991 | 3.6908 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.2836 | 7.4996 | 12.2061 | 5.7825 | 16.3615 | 8.1323 | 28.6151 | 3.7541 | 33.681 | 4.7202 | 35.943 | 7.5071 | 52.0359 | 5.495 | 57.1646 | 8.8804 | 77.7061 | 5.9706 | 117.088 | 3.7428 | 157.737 | 2.6375 | 190.553 | 4.0182 | 244.186 | 3.8299 | 318.28 | 4.0749 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.2086 | 8.6352 | 11.869 | 6.442 | 15.9895 | 8.9338 | 27.6309 | 4.1365 | 32.6529 | 5.1544 | 35.0205 | 8.4304 | 50.5991 | 6.0912 | 55.4196 | 10.2046 | 75.7875 | 6.7791 | 113.855 | 4.1614 | 151.098 | 2.9798 | 186.407 | 4.3704 | 240.07 | 4.1822 | 312.29 | 4.4099 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.1468 | 10.1031 | 11.6573 | 6.9507 | 15.72 | 9.7361 | 26.7339 | 4.5351 | 31.8786 | 5.5115 | 34.1217 | 9.4957 | 49.2512 | 6.6982 | 54.1595 | 11.6446 | 73.4742 | 8.1079 | 111.267 | 4.5533 | 145.61 | 3.3563 | 181.804 | 4.7915 | 234.377 | 4.636 | 305.8 | 4.83 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.0918 | 12.1441 | 11.3695 | 7.7125 | 15.4396 | 10.6317 | 25.8661 | 5.012 | 31.0915 | 5.9527 | 33.3459 | 10.5681 | 48.0352 | 7.3879 | 53.3532 | 13.1292 | 71.5169 | 9.6296 | 108.846 | 5.0827 | 140.742 | 3.7503 | 177.848 | 5.2375 | 229.966 | 5.1031 | 299.445 | 5.306 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
6.0372 | 14.5974 | 11.0666 | 8.6007 | 15.2097 | 11.5634 | 24.8022 | 5.6454 | 30.3845 | 6.4356 | 32.7838 | 11.7499 | 46.943 | 8.1567 | 52.3491 | 15.2235 | 69.6118 | 11.6679 | 106.584 | 5.7136 | 136.856 | 4.0953 | 173.804 | 5.8348 | 225.864 | 5.6908 | 292.929 | 5.8935 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.9951 | 17.4413 | 10.8258 | 9.6008 | 15.0283 | 12.7158 | 24.1415 | 6.134 | 29.7829 | 6.9091 | 32.2957 | 12.9986 | 46.1056 | 8.9517 | 51.4152 | 18.0626 | 67.8931 | 14.1518 | 103.952 | 6.5133 | 134.146 | 4.4231 | 170.363 | 6.4163 | 221.17 | 6.4292 | 287.992 | 6.4485 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.9532 | 21.1755 | 10.6008 | 10.814 | 14.8342 | 14.1235 | 23.4749 | 6.6915 | 29.0766 | 7.5221 | 31.8467 | 14.952 | 45.3284 | 9.8734 | 50.5991 | 22.0397 | 66.3493 | 17.7049 | 102.404 | 7.2852 | 131.621 | 4.7628 | 166.823 | 7.1624 | 215.709 | 7.3879 | 282.854 | 7.1053 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.9532 | 24.7505 | 10.4013 | 12.5515 | 14.6719 | 15.6402 | 22.8954 | 7.2416 | 28.5579 | 8.0998 | 31.3726 | 17.865 | 44.743 | 10.7816 | 49.9956 | 26.4921 | 65.4924 | 19.9423 | 100.076 | 8.5066 | 129.403 | 5.1647 | 163.683 | 7.9633 | 211.649 | 8.3549 | 277.253 | 7.8605 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.9354 | 30.2001 | 10.2875 | 13.8577 | 14.5114 | 17.5112 | 22.4644 | 7.8056 | 27.9924 | 8.7482 | 31.0604 | 20.3452 | 43.9009 | 12.2907 | 49.5972 | 32.1639 | 64.9056 | 22.5074 | 98.1929 | 9.8143 | 127.222 | 5.6173 | 160.442 | 8.9338 | 207.666 | 9.4863 | 270.949 | 9.0507 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.9236 | 36.8497 | 10.1648 | 15.5311 | 14.3814 | 19.7044 | 22.0416 | 8.38 | 27.4656 | 9.6296 | 30.7514 | 24.2847 | 43.0316 | 14.2655 | 49.4486 | 39.7197 | 64.0673 | 26.4656 | 96.2485 | 11.3798 | 125.077 | 6.1709 | 158.211 | 9.9428 | 203.758 | 10.9884 | 265.85 | 10.1537 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.9176 | 49.9912 | 10.0838 | 17.4239 | 14.2525 | 22.1945 | 21.6918 | 9.0961 | 27.0567 | 10.3278 | 30.5674 | 28.5268 | 42.3909 | 16.508 | 49.4981 | 49.0013 | 63.4933 | 30.4123 | 94.5316 | 13.3677 | 122.846 | 6.8953 | 155.233 | 11.1656 | 199.923 | 12.7285 | 260.846 | 11.5518 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.894 | 63.8061 | 10.0135 | 19.7242 | 14.1389 | 25.2 | 21.3475 | 9.913 | 26.6272 | 11.3684 | 30.5063 | 33.6444 | 41.7181 | 19.6258 | 49.5476 | 65.03 | 62.9244 | 35.2987 | 92.7524 | 16.2297 | 120.534 | 7.7125 | 152.77 | 12.5264 | 195.964 | 15.1325 | 255.937 | 13.3543 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8881 | 90.0036 | 9.9636 | 22.0397 | 14.0403 | 28.584 | 20.9876 | 10.8682 | 26.3623 | 12.2294 | 30.4454 | 39.1675 | 41.3443 | 23.2858 | 49.5972 | 85.443 | 62.2983 | 43.4168 | 90.4623 | 21.1755 | 118.739 | 8.5749 | 150.796 | 13.969 | 191.7 | 18.135 | 251.623 | 15.2846 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8881 | 116.03 | 9.8941 | 25.4788 | 13.9563 | 32.0035 | 20.7373 | 11.7616 | 26.1261 | 13.2479 | 30.2935 | 47.08 | 40.9329 | 27.3809 | 49.5972 | 123.451 | 61.7401 | 54.2091 | 89.2047 | 25.4788 | 116.855 | 9.6296 | 148.7 | 15.4382 | 187.716 | 22.7564 | 247.629 | 17.3544 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 163.016 | 9.8743 | 29.8996 | 13.859 | 37.1456 | 20.4899 | 12.895 | 25.7886 | 15.1476 | 30.1726 | 56.9884 | 40.5662 | 32.7809 | 49.5972 | 169.839 | 61.2482 | 67.6839 | 88.2288 | 29.9895 | 115.115 | 10.814 | 146.779 | 17.4239 | 184.367 | 28.4699 | 243.698 | 20.0022 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 213.119 | 9.8644 | 34.5306 | 13.8175 | 42.8561 | 20.2658 | 14.011 | 25.5831 | 17.3891 | 30.0822 | 69.0512 | 40.3638 | 38.9332 | 49.5972 | 227.887 | 60.8209 | 88.3096 | 87.0893 | 36.7393 | 113.628 | 12.0232 | 145.028 | 19.6651 | 181.079 | 34.8428 | 238.634 | 24.1635 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8705 | 316.351 | 9.8644 | 40.6438 | 13.7899 | 49.3456 | 20.1244 | 15.3919 | 25.4556 | 20.1629 | 29.9921 | 84.5928 | 40.1625 | 49.2962 | 49.6468 | 306.081 | 60.3363 | 117.196 | 86.3953 | 42.9848 | 112.048 | 13.9133 | 143.299 | 22.3281 | 178.026 | 45.8717 | 235.316 | 27.7114 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 409.875 | 9.8644 | 49.4938 | 13.7899 | 57.5036 | 20.004 | 16.9428 | 25.481 | 24.0671 | 29.9322 | 98.0865 | 40.0823 | 60.0903 | 49.5972 | 429.17 | 60.1556 | 161.233 | 85.3648 | 52.7122 | 110.38 | 15.9721 | 141.731 | 25.9415 | 175.2 | 59.1957 | 232.045 | 32.0676 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8764 | 484.372 | 9.8644 | 59.7906 | 13.7761 | 68.9822 | 19.9043 | 18.6313 | 25.481 | 28.6985 | 29.9322 | 119.923 | 40.0823 | 76.6193 | 49.5972 | 520.533 | 59.8555 | 210.366 | 84.6 | 67.1446 | 109.063 | 18.706 | 140.18 | 29.1614 | 172.592 | 75.5541 | 228.819 | 37.0344 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8764 | 543.404 | 9.8644 | 74.5782 | 13.7761 | 82.0107 | 19.8844 | 20.9229 | 25.5065 | 34.9475 | 29.9322 | 146.767 | 40.0422 | 103.736 | 49.5972 | 577.006 | 59.8555 | 270.386 | 83.6745 | 85.8713 | 107.655 | 21.9078 | 138.508 | 34.2897 | 170.363 | 94.9025 | 225.638 | 42.8132 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8644 | 93.6767 | 13.7761 | 100.368 | 19.8645 | 23.5905 | 25.532 | 45.3698 | 29.9322 | 184.352 | 40.0022 | 130.692 | 49.5972 | 602.961 | 59.8555 | 332.57 | 83.0908 | 104.883 | 106.584 | 25.3263 | 136.856 | 40.7659 | 167.994 | 124.194 | 222.946 | 48.4168 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8644 | 118.611 | 13.7761 | 118.019 | 19.8248 | 27.7114 | 25.5831 | 58.8415 | 29.9322 | 229.258 | 39.8425 | 176.417 | 49.5972 | 602.961 | 59.9154 | 414.823 | 82.5937 | 126.576 | 105.629 | 29.5725 | 135.088 | 53.4554 | 166.157 | 159.309 | 220.287 | 56.2524 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8644 | 148.985 | 13.7761 | 137.944 | 19.8248 | 32.3252 | 25.5831 | 74.5782 | 29.9322 | 271.47 | 39.8027 | 238.615 | 49.5972 | 602.961 | 59.9154 | 491.201 | 82.1818 | 155.066 | 104.473 | 35.7964 | 134.012 | 64.0618 | 164.833 | 207.027 | 217.442 | 64.4473 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 202.118 | 13.7761 | 162.853 | 19.8446 | 38.5073 | 25.6344 | 86.7343 | 29.9322 | 366.813 | 39.7231 | 305.47 | 49.5972 | 602.961 | 59.9154 | 566.147 | 81.6902 | 201.512 | 103.641 | 42.7277 | 132.944 | 76.3898 | 163.683 | 258.747 | 214.633 | 76.6193 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 259.006 | 13.7761 | 201.714 | 19.8446 | 45.6885 | 25.6087 | 108.077 | 29.9322 | 453.435 | 39.6834 | 375.347 | 49.5972 | 602.961 | 59.9154 | 608.413 | 81.2827 | 255.66 | 102.815 | 51.8756 | 131.753 | 98.0865 | 162.541 | 325.985 | 212.285 | 88.7523 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 319.53 | 13.7761 | 248.105 | 19.8446 | 56.6475 | 25.6087 | 129.651 | 29.9322 | 529.458 | 39.525 | 473.832 | 49.5972 | 602.961 | 59.9154 | 608.413 | 80.7158 | 336.249 | 102.302 | 61.1206 | 130.965 | 115.451 | 161.407 | 415.238 | 209.963 | 101.58 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 399.755 | 13.7761 | 305.775 | 19.8446 | 68.2958 | 25.66 | 164.49 | 29.9322 | 572.981 | 39.4461 | 550.514 | 49.5972 | 602.961 | 59.9154 | 608.413 | 80.3132 | 422.358 | 101.487 | 74.8772 | 129.921 | 141.012 | 160.442 | 498.624 | 207.458 | 122.101 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 488.751 | 13.7761 | 366.446 | 19.8645 | 80.0658 | 25.66 | 205.583 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.9126 | 513.81 | 101.183 | 86.9949 | 129.403 | 170.69 | 159.961 | 559.393 | 205.394 | 146.767 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 571.265 | 13.7761 | 436.092 | 19.8645 | 94.2405 | 25.66 | 248.353 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.753 | 578.161 | 100.678 | 105.937 | 129.015 | 216.34 | 159.322 | 605.984 | 203.35 | 178.19 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7761 | 503.635 | 19.8844 | 113.846 | 25.66 | 301.826 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 100.276 | 127.466 | 128.886 | 278.621 | 159.322 | 605.984 | 201.327 | 209.108 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 573.555 | 19.8844 | 134.942 | 25.6857 | 377.606 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 99.9763 | 173.79 | 128.5 | 359.549 | 159.322 | 605.984 | 200.123 | 251.602 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 609.021 | 19.8844 | 155.999 | 25.6857 | 467.244 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 99.6769 | 223.598 | 128.5 | 461.21 | 159.322 | 605.984 | 198.926 | 299.122 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 609.021 | 19.8645 | 186.391 | 25.7114 | 552.721 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 99.4777 | 282.549 | 128.5 | 569.554 | 159.322 | 605.984 | 197.933 | 362.075 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 609.021 | 19.8844 | 222.928 | 25.7371 | 609.631 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 99.0806 | 347.878 | 128.372 | 601.757 | 159.322 | 605.984 | 196.749 | 446.684 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 609.021 | 19.8844 | 282.266 | 25.7371 | 609.631 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 98.6851 | 424.475 | 128.372 | 601.757 | 159.322 | 605.984 | 195.964 | 553.827 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 609.021 | 19.8844 | 346.836 | 25.7371 | 609.631 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 98.3895 | 488.262 | 128.372 | 601.757 | 159.322 | 605.984 | 195.182 | 601.155 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 609.021 | 19.8844 | 423.627 | 25.7371 | 609.631 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 98.0947 | 568.984 | 128.372 | 601.757 | 159.322 | 605.984 | 195.182 | 601.155 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 609.021 | 19.8844 | 500.122 | 25.7371 | 609.631 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 97.9967 | 602.359 | 128.372 | 601.757 | 159.322 | 605.984 | 195.182 | 601.155 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 609.021 | 19.9043 | 565.015 | 25.7371 | 609.631 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 97.9967 | 602.359 | 128.372 | 601.757 | 159.322 | 605.984 | 195.182 | 601.155 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665
5.8822 | 585.727 | 9.8546 | 605.984 | 13.7623 | 609.021 | 19.9043 | 599.355 | 25.7371 | 609.631 | 29.9322 | 600.554 | 39.3672 | 602.961 | 49.5972 | 602.961 | 59.9154 | 608.413 | 79.5936 | 609.021 | 97.9967 | 602.359 | 128.372 | 601.757 | 159.322 | 605.984 | 195.182 | 601.155 | 274.769 | 605.984 | 328.63 | 602.961 | 381.05 | 600.554 | 440.509 | 610.241 | 551.66 | 607.197 | 657.82 | 612.686 | 789.13 | 522.097 | 988.245 | 521.054 | 1187.88 | 523.665