## 680-9
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
S&C Standard ("E") Speed (TCC 680-9) | [9 empty] | S&C Standard ("E") Speed (TCC 680-9) | [9 empty] | S&C Standard ("E") Speed (TCC 680-9)
Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus.
25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 400E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
1326.01 | 0.01 | 1462.54 | 0.01 | 1877.93 | 0.01 | 2289.13 | 0.01 | 3133.57 | 0.01 | 3967.65 | 0.01 | 4929.18 | 0.01 | 6377.2165 | 0.01 | 7769.24 | 0.01 | 8724.83 | 0.01 | 9527.41 | 0.01 | 11406.3 | 0.01 | 14015.6 | 0.01 | 17924.5 | 0.01
1295.86 | 0.01045 | 1436.45 | 0.010377 | 1849.98 | 0.010325 | 2261.83 | 0.010284 | 3090.01 | 0.010336 | 3916.4 | 0.010325 | 4855.8 | 0.010377 | 6282.2734 | 0.010346 | 7577.42 | 0.010492 | 8509.41 | 0.010544 | 9135.54 | 0.010942 | 10372.6 | 0.012008 | 13601.3 | 0.010629 | 17394.8 | 0.010587
1222.83 | 0.011747 | 1396.78 | 0.010964 | 1798.89 | 0.01092 | 2208.19 | 0.010811 | 2980.74 | 0.011041 | 3800.65 | 0.010942 | 4731.17 | 0.010931 | 6048.0181 | 0.01114 | 7079.28 | 0.011996 | 8299.31 | 0.011063 | 8475.44 | 0.012763 | 9208.92 | 0.01525 | 12719.9 | 0.012129 | 16563 | 0.011688
1151.62 | 0.013271 | 1343.36 | 0.011829 | 1724.91 | 0.011829 | 2138.65 | 0.011514 | 2875.35 | 0.011889 | 3543.71 | 0.012599 | 4573.02 | 0.011688 | 5667.393 | 0.012687 | 6574.33 | 0.013882 | 8005.85 | 0.011901 | 7792.59 | 0.015038 | 7863.04 | 0.020938 | 11292.8 | 0.01545 | 15567.2 | 0.013152
1053.56 | 0.015841 | 1277.84 | 0.0131 | 1649.01 | 0.012956 | 2060.96 | 0.012386 | 2762.6 | 0.012827 | 3258.19 | 0.014903 | 4354.34 | 0.012879 | 5332.0173 | 0.014333 | 6074.94 | 0.016274 | 7691.94 | 0.012905 | 7086.37 | 0.018239 | 6876.93 | 0.027456 | 9946.02 | 0.019877 | 14852.5 | 0.014463
980.371 | 0.018276 | 1197.42 | 0.014933 | 1559.2 | 0.014463 | 1984.11 | 0.013378 | 2659.59 | 0.013868 | 3025.79 | 0.017194 | 4141.98 | 0.014248 | 5051.7092 | 0.015936 | 5613.49 | 0.01906 | 7397.73 | 0.013938 | 6444.15 | 0.022078 | 5767.12 | 0.039001 | 8794.91 | 0.025396 | 14099.9 | 0.016032
897.785 | 0.021641 | 1120.94 | 0.017023 | 1453.79 | 0.016686 | 1893.02 | 0.014652 | 2464.95 | 0.016112 | 2787.58 | 0.020299 | 3789.27 | 0.017023 | 4672.6372 | 0.018589 | 5064.08 | 0.023326 | 7058.08 | 0.015265 | 5825.08 | 0.026939 | 5064.08 | 0.050531 | 7730.49 | 0.033003 | 13425.7 | 0.017665
829.589 | 0.02532 | 1042.03 | 0.01968 | 1298.45 | 0.020792 | 1781 | 0.01657 | 2296.01 | 0.018571 | 2542.56 | 0.024376 | 3536.63 | 0.019503 | 4387.34 | 0.021149 | 4684.1 | 0.027237 | 6788.11 | 0.01657 | 5286.59 | 0.03274 | 4293.8 | 0.070287 | 6822.14 | 0.042631 | 12669.1 | 0.019838
768.877 | 0.029417 | 962.882 | 0.023048 | 1185.51 | 0.024968 | 1685.69 | 0.018441 | 2125.85 | 0.021641 | 2365.93 | 0.028039 | 3261.45 | 0.02291 | 4086.6201 | 0.02423 | 4349.99 | 0.031519 | 6418.43 | 0.018515 | 4759.64 | 0.040189 | 3677.28 | 0.095927 | 6105.4 | 0.053016 | 11919.4 | 0.022412
709.053 | 0.034625 | 898.683 | 0.026432 | 1089.99 | 0.029506 | 1576.44 | 0.021064 | 1915.87 | 0.026485 | 2221.48 | 0.031868 | 3034.88 | 0.026406 | 3761.1278 | 0.02872 | 3943.91 | 0.038536 | 6142.14 | 0.020198 | 4306.7 | 0.049136 | 3158.74 | 0.12962 | 5307.78 | 0.070358 | 11124.7 | 0.025805
644.15 | 0.041955 | 822.979 | 0.031519 | 1010.22 | 0.034384 | 1496.56 | 0.023443 | 1752.73 | 0.031677 | 2083.76 | 0.036219 | 2743.33 | 0.032414 | 3440.8338 | 0.034212 | 3579.32 | 0.046646 | 5830.91 | 0.022412 | 3808.26 | 0.062714 | 2779.23 | 0.1676 | 4707.58 | 0.089621 | 10248.9 | 0.030313
596.412 | 0.048744 | 755.161 | 0.037472 | 926.979 | 0.040796 | 1393.99 | 0.026939 | 1573.3 | 0.039197 | 1942.88 | 0.041454 | 2509.72 | 0.03869 | 2961.5294 | 0.046136 | 3258.19 | 0.056125 | 5546.53 | 0.024794 | 3452.76 | 0.07637 | 2394.5 | 0.2292 | 3947.86 | 0.12718 | 9603.93 | 0.034522
551.108 | 0.056974 | 685.351 | 0.045403 | 848.043 | 0.048696 | 1328.66 | 0.029654 | 1417.89 | 0.048308 | 1786.35 | 0.049136 | 2246.05 | 0.048019 | 2631.8801 | 0.058299 | 2924.64 | 0.069518 | 5239.22 | 0.02776 | 3127.31 | 0.093092 | 2119.48 | 0.30145 | 3463.13 | 0.16461 | 8945.7 | 0.039709
491.731 | 0.071492 | 624.487 | 0.054794 | 778.938 | 0.057661 | 1265.13 | 0.032805 | 1298.45 | 0.057546 | 1632.6 | 0.058533 | 2067.15 | 0.056917 | 2364.7966 | 0.071779 | 2641.04 | 0.08508 | 4993.68 | 0.030496 | 2881.1 | 0.10957 | 1891.13 | 0.39409 | 3050.1 | 0.21328 | 8282.73 | 0.046228
449.408 | 0.085849 | 583.434 | 0.062652 | 708.345 | 0.069588 | 1202.22 | 0.036255 | 1190.26 | 0.068758 | 1519.18 | 0.067599 | 1861.11 | 0.069937 | 2146.1626 | 0.087146 | 2314.45 | 0.11045 | 4754.89 | 0.033501 | 2646.33 | 0.12949 | 1670.58 | 0.53947 | 2694.39 | 0.2744 | 7684.25 | 0.053763
412.787 | 0.10115 | 545.625 | 0.071564 | 648.026 | 0.082896 | 1127.69 | 0.041165 | 1087.82 | 0.082154 | 1423.58 | 0.076906 | 1709.45 | 0.082648 | 1981.14 | 0.10227 | 2056.84 | 0.14013 | 4509.44 | 0.03736 | 2425.83 | 0.15441 | 1502.56 | 0.71095 | 2328.38 | 0.36635 | 7186.27 | 0.061472
382.96 | 0.11764 | 498.165 | 0.085935 | 584.018 | 0.10206 | 1073.77 | 0.045403 | 994.192 | 0.098651 | 1295.86 | 0.092628 | 1563.88 | 0.098651 | 1841.6435 | 0.11764 | 1861.11 | 0.17014 | 4280.94 | 0.04133 | 2175.31 | 0.19125 | 1363.66 | 0.9435 | 2050.68 | 0.47847 | 6633.77 | 0.072211
355.289 | 0.13654 | 466.348 | 0.097865 | 530.559 | 0.12367 | 1016.3 | 0.050734 | 866.04 | 0.12936 | 1196.23 | 0.10848 | 1435.01 | 0.11717 | 1723.9977 | 0.1345 | 1690.75 | 0.20574 | 4064.02 | 0.045768 | 1996.05 | 0.2276 | 1241.32 | 1.2596 | 1874.18 | 0.5891 | 6222.51 | 0.081826
322.445 | 0.16511 | 430.493 | 0.11496 | 485.38 | 0.14761 | 954.255 | 0.057777 | 789.13 | 0.15612 | 1102.05 | 0.1268 | 1295.86 | 0.14382 | 1589.8397 | 0.15753 | 1532.92 | 0.24904 | 3865.82 | 0.050481 | 1818.79 | 0.27468 | 1158.55 | 1.587 | 1737.02 | 0.71095 | 5784.45 | 0.095258
303.363 | 0.1869 | 397.395 | 0.13504 | 441.391 | 0.17797 | 901.384 | 0.064689 | 719.769 | 0.18784 | 998.177 | 0.15394 | 1183.14 | 0.17271 | 1483.82 | 0.18102 | 1337.99 | 0.32721 | 3647.98 | 0.056689 | 1667.24 | 0.33016 | 1064.14 | 2.2008 | 1603.47 | 0.87445 | 5474.89 | 0.10538
282.571 | 0.21477 | 367.944 | 0.15721 | 402.193 | 0.21413 | 820.514 | 0.077913 | 663.103 | 0.22132 | 888.852 | 0.19395 | 1089.99 | 0.2043 | 1365.6067 | 0.21328 | 1205.83 | 0.40246 | 3449.31 | 0.063408 | 1576.44 | 0.3704 | 995.187 | 2.9413 | 1523.75 | 1.0119 | 5069.15 | 0.12416
260.325 | 0.25179 | 340.676 | 0.18339 | 354.579 | 0.27578 | 764.277 | 0.089442 | 618.892 | 0.25356 | 805.877 | 0.23571 | 1026.52 | 0.23058 | 1282.2072 | 0.24095 | 1069.48 | 0.51522 | 3264.72 | 0.070781 | 1484.64 | 0.42267 | 933.491 | 4.0142 | 1436.45 | 1.1875 | 4769.17 | 0.14126
238.157 | 0.30054 | 319.236 | 0.20926 | 329.947 | 0.31977 | 716.896 | 0.10155 | 583.434 | 0.28589 | 723.377 | 0.29108 | 968.677 | 0.26076 | 1194.3117 | 0.27688 | 969.646 | 0.63562 | 3086.92 | 0.079249 | 1416.48 | 0.469 | 898.683 | 5.0725 | 1347.39 | 1.4288 | 4513.95 | 0.15832
219.627 | 0.35304 | 294.398 | 0.24557 | 306.719 | 0.36893 | 659.796 | 0.12013 | 542.903 | 0.33016 | 661.779 | 0.34571 | 914.092 | 0.29489 | 1125.8764 | 0.31125 | 887.076 | 0.77868 | 2904.24 | 0.089442 | 1350.09 | 0.52405 | 860.859 | 6.8747 | 1248.79 | 1.8037 | 4154.42 | 0.18916
193.24 | 0.45241 | 275.595 | 0.28079 | 291.468 | 0.41018 | 606.637 | 0.14197 | 510.776 | 0.37077 | 623.863 | 0.38939 | 866.04 | 0.33182 | 1048.695 | 0.35982 | 808.298 | 0.96835 | 2748.82 | 0.099942 | 1290.68 | 0.58557 | 837.089 | 9.3544 | 1169.03 | 2.2498 | 3808.26 | 0.22874
174.85 | 0.55202 | 249.368 | 0.34295 | 277.808 | 0.45196 | 525.28 | 0.18878 | 482.959 | 0.41347 | 591.068 | 0.42949 | 801.056 | 0.39056 | 967.086 | 0.42352 | 743.918 | 1.1887 | 2586.16 | 0.1128 | 1230.19 | 0.65628 | 812.35 | 12.464 | 1104.26 | 2.77 | 3497.94 | 0.27883
159.641 | 0.65892 | 230.657 | 0.40165 | 267.45 | 0.49009 | 458.487 | 0.24804 | 463.095 | 0.45106 | 560.557 | 0.47847 | 756.673 | 0.4408 | 902.588 | 0.49009 | 688.786 | 1.4519 | 2445.31 | 0.12554 | 1178.42 | 0.7326 | 790.71 | 17.8293 | 1064.14 | 3.2409 | 3238.7 | 0.33448
146.926 | 0.77402 | 210.173 | 0.4828 | 252.884 | 0.54872 | 415.686 | 0.30145 | 445.381 | 0.49058 | 534.286 | 0.52826 | 713.321 | 0.5025 | 838.1697 | 0.57398 | 637.74 | 1.7822 | 2282.27 | 0.14397 | 1118.7 | 0.8343 | 766.574 | 26.3336 | 1017.32 | 4.1323 | 2912.97 | 0.43035
137.13 | 0.88767 | 192.276 | 0.57398 | 242.968 | 0.5974 | 372.386 | 0.37638 | 427.918 | 0.53091 | 501.664 | 0.6016 | 673.125 | 0.57055 | 797.2725 | 0.63816 | 582.268 | 2.3346 | 2142.93 | 0.16346 | 1065.21 | 0.95108 | 741.69 | 38.7778 | 975.481 | 5.4241 | 2702.49 | 0.51625
128.115 | 1.0252 | 171.56 | 0.72169 | 234.377 | 0.64522 | 347.21 | 0.43424 | 400.587 | 0.60947 | 473.869 | 0.67898 | 638.378 | 0.64072 | 759.8889 | 0.7074 | 539.116 | 3.0007 | 2002.05 | 0.1869 | 1015.29 | 1.0788 | 718.331 | 55.1937 | 940.988 | 7.1983 | 2550.2 | 0.6004
119.454 | 1.1816 | 157.737 | 0.86316 | 224.512 | 0.70669 | 328.63 | 0.4828 | 379.909 | 0.68512 | 445.827 | 0.77479 | 609.069 | 0.71166 | 723.513 | 0.78887 | 499.162 | 4.2242 | 1877.93 | 0.21158 | 973.532 | 1.2151 | 694.319 | 82.0927 | 908.624 | 9.8635 | 2404.09 | 0.69826
111.936 | 1.3551 | 148.998 | 0.9732 | 213.349 | 0.78808 | 312.602 | 0.53357 | 354.225 | 0.79919 | 419.444 | 0.88501 | 569.598 | 0.82848 | 695.7994 | 0.85885 | 469.623 | 5.9408 | 1772.11 | 0.23784 | 932.557 | 1.3824 | 667.761 | 126.45 | 873.869 | 14.0953 | 2298.31 | 0.79282
106.264 | 1.5187 | 139.9 | 1.1172 | 201.327 | 0.89748 | 300.345 | 0.58091 | 334.264 | 0.90923 | 399.387 | 0.98594 | 543.446 | 0.92389 | 667.1399 | 0.94633 | 447.614 | 8.2058 | 1678.96 | 0.26417 | 892.415 | 1.5949 | 642.22 | 192.068 | 850.591 | 18.2624 | 2184.03 | 0.9147
99.9763 | 1.7504 | 132.149 | 1.2685 | 189.413 | 1.0293 | 285.697 | 0.64522 | 316.06 | 1.0293 | 385.65 | 1.0713 | 510.776 | 1.0723 | 640.298 | 1.0448 | 433.084 | 10.8791 | 1600.27 | 0.29195 | 856.566 | 1.831 | 623.24 | 281.702 | 825.452 | 26.4391 | 2052.73 | 1.1006
95.1956 | 1.9539 | 124.578 | 1.4548 | 180.536 | 1.1478 | 270.949 | 0.71953 | 297.654 | 1.178 | 370.9 | 1.1792 | 482.476 | 1.2298 | 613.9625 | 1.1605 | 422.391 | 13.8994 | 1525.27 | 0.32395 | 823.803 | 2.1251 | 606.637 | 386.392 | 809.916 | 35.3694 | 1944.83 | 1.3163
90.0112 | 2.2341 | 118.858 | 1.6223 | 173.111 | 1.2622 | 258.251 | 0.796 | 282.007 | 1.3376 | 359.219 | 1.266 | 458.487 | 1.3949 | 595.2216 | 1.2571 | 413.613 | 17.9008 | 1442.2 | 0.36525 | 795.468 | 2.4617 | 591.659 | 505.654 | 795.468 | 49.0504 | 1826.08 | 1.6272
84.8541 | 2.5724 | 113.174 | 1.8255 | 166.489 | 1.3935 | 244.43 | 0.89569 | 269.598 | 1.4856 | 347.558 | 1.3687 | 441.833 | 1.5278 | 573.6002 | 1.3907 | 403.401 | 24.5533 | 1351.44 | 0.42056 | 771.959 | 2.8231 | 583.434 | 607.197 | 782.06 | 66.0788 | 1738.76 | 2.0175
81.6902 | 2.8316 | 107.978 | 2.0623 | 160.281 | 1.5263 | 233.441 | 0.9889 | 256.706 | 1.6885 | 333.93 | 1.5141 | 429.633 | 1.6468 | 557.2048 | 1.4946 | 395.018 | 32.6827 | 1280.4 | 0.47371 | 743.918 | 3.3698 | 583.434 | 607.197 | 767.341 | 90.1838 | 1677.28 | 2.4323
77.3959 | 3.2539 | 102.815 | 2.3463 | 155.389 | 1.6567 | 222.501 | 1.0973 | 246.148 | 1.8754 | 322.445 | 1.66 | 414.856 | 1.8164 | 539.1173 | 1.6452 | 389.916 | 44.427 | 1220.39 | 0.52932 | 719.769 | 3.9703 | 583.434 | 607.197 | 767.341 | 119.683 | 1616.35 | 3.0308
73.4007 | 3.7691 | 98.2911 | 2.6349 | 150.194 | 1.8073 | 211.649 | 1.2286 | 239.351 | 2.0255 | 311.043 | 1.82 | 399.787 | 2.0074 | 518.4969 | 1.8438 | 383.727 | 63.045 | 1145.88 | 0.6113 | 695.013 | 4.8883 | 583.434 | 607.197 | 742.432 | 162.69 | 1565.45 | 3.7654
69.4033 | 4.4187 | 94.2484 | 2.9708 | 145.901 | 1.9422 | 203.35 | 1.3578 | 231.581 | 2.2185 | 300.645 | 1.9914 | 382.96 | 2.2633 | 502.1673 | 2.0215 | 379.909 | 81.765 | 1103.15 | 0.66954 | 672.452 | 5.9885 | 583.434 | 607.197 | 731.378 | 212.906 | 1525.27 | 4.599
66.9492 | 4.9424 | 90.7341 | 3.3262 | 141.165 | 2.1337 | 193.433 | 1.5293 | 224.512 | 2.4421 | 289.435 | 2.2141 | 370.158 | 2.4964 | 488.3019 | 2.2052 | 376.882 | 110.371 | 1056.72 | 0.7474 | 650.623 | 7.3953 | 583.434 | 607.197 | 723.377 | 261.086 | 1490.59 | 5.7193
64.5819 | 5.5392 | 87.4383 | 3.7279 | 136.719 | 2.3299 | 186.034 | 1.6851 | 218.095 | 2.6614 | 277.253 | 2.4989 | 358.143 | 2.7562 | 476.7223 | 2.3913 | 374.253 | 141.295 | 1006.19 | 0.84776 | 632.659 | 9.2059 | 583.434 | 607.197 | 712.608 | 337.259 | 1462.54 | 6.7859
62.2983 | 6.2641 | 84.7693 | 4.1614 | 131.621 | 2.5905 | 178.919 | 1.8605 | 210.594 | 2.9442 | 269.059 | 2.7534 | 345.479 | 3.0644 | 466.8149 | 2.5673 | 372.014 | 177.124 | 967.708 | 0.93973 | 619.511 | 11.1768 | 583.434 | 607.197 | 701.998 | 431.321 | 1423.58 | 8.5664
60.3363 | 7.0628 | 82.3463 | 4.6499 | 126.967 | 2.9004 | 172.592 | 2.05 | 204.165 | 3.2441 | 258.509 | 3.1107 | 335.268 | 3.3731 | 457.1138 | 2.809 | 368.312 | 231.563 | 929.764 | 1.0479 | 604.216 | 14.0953 | 583.434 | 607.197 | 695.013 | 513.81 | 1395.39 | 10.4734
58.6703 | 7.9236 | 80.1527 | 5.2218 | 122.111 | 3.2734 | 165.163 | 2.316 | 196.749 | 3.6105 | 252.379 | 3.4104 | 326.991 | 3.6908 | 448.0631 | 3.0644 | 366.109 | 300.621 | 895.096 | 1.1686 | 584.602 | 19.567 | 583.434 | 607.197 | 690.856 | 558.834 | 1365.02 | 12.8436
57.1646 | 8.8804 | 77.7061 | 5.9706 | 117.088 | 3.7428 | 157.737 | 2.6375 | 190.553 | 4.0182 | 244.186 | 3.8299 | 318.28 | 4.0749 | 439.1906 | 3.3296 | 363.919 | 377.606 | 864.309 | 1.2993 | 568.46 | 26.4127 | 583.434 | 607.197 | 688.786 | 600.554 | 1332.65 | 15.829
55.4196 | 10.2046 | 75.7875 | 6.7791 | 113.855 | 4.1614 | 151.098 | 2.9798 | 186.407 | 4.3704 | 240.07 | 4.1822 | 312.29 | 4.4099 | 429.6485 | 3.6761 | 362.466 | 478.594 | 829.589 | 1.4753 | 555.535 | 34.5997 | 583.434 | 607.197 | 688.786 | 600.554 | 1306.26 | 19.1221
54.1595 | 11.6446 | 73.4742 | 8.1079 | 111.267 | 4.5533 | 145.61 | 3.3563 | 181.804 | 4.7915 | 234.377 | 4.636 | 305.8 | 4.83 | 421.5758 | 4.0424 | 361.742 | 577.006 | 796.264 | 1.6885 | 541.819 | 47.316 | 583.434 | 607.197 | 688.786 | 600.554 | 1272.74 | 24.3576
53.3532 | 13.1292 | 71.5169 | 9.6296 | 108.846 | 5.0827 | 140.742 | 3.7503 | 177.848 | 5.2375 | 229.966 | 5.1031 | 299.445 | 5.306 | 414.8973 | 4.401 | 361.742 | 606.59 | 761.988 | 1.9578 | 530.559 | 63.1712 | 583.434 | 607.197 | 688.786 | 600.554 | 1248.79 | 29.1031
52.3491 | 15.2235 | 69.6118 | 11.6679 | 106.584 | 5.7136 | 136.856 | 4.0953 | 173.804 | 5.8348 | 225.864 | 5.6908 | 292.929 | 5.8935 | 408.7198 | 4.7486 |  |  | 740.208 | 2.1986 | 520.053 | 88.1332 | 583.434 | 607.197 | 688.786 | 600.554 | 1219.17 | 36.0478
51.4152 | 18.0626 | 67.8931 | 14.1518 | 103.952 | 6.5133 | 134.146 | 4.4231 | 170.363 | 6.4163 | 221.17 | 6.4292 | 287.992 | 6.4485 | 402.2453 | 5.1802 |  |  | 716.18 | 2.4989 | 510.776 | 120.163 | 583.434 | 607.197 | 688.786 | 600.554 | 1193.84 | 44.1171
50.5991 | 22.0397 | 66.3493 | 17.7049 | 102.404 | 7.2852 | 131.621 | 4.7628 | 166.823 | 7.1624 | 215.709 | 7.3879 | 282.854 | 7.1053 | 396.25 | 5.6398 |  |  | 695.709 | 2.8231 | 503.675 | 161.071 | 583.434 | 607.197 | 688.786 | 600.554 | 1160.87 | 57.7341
49.9956 | 26.4921 | 65.4924 | 19.9423 | 100.076 | 8.5066 | 129.403 | 5.1647 | 163.683 | 7.9633 | 211.649 | 8.3549 | 277.253 | 7.8605 | 390.3567 | 6.208 |  |  | 677.176 | 3.199 | 497.17 | 227.659 | 583.434 | 607.197 | 688.786 | 600.554 | 1134.48 | 71.5824
49.5972 | 32.1639 | 64.9056 | 22.5074 | 98.1929 | 9.8143 | 127.222 | 5.6173 | 160.442 | 8.9338 | 207.666 | 9.4863 | 270.949 | 9.0507 | 383.0208 | 6.9716 |  |  | 659.796 | 3.6322 | 491.731 | 310.397 | 583.434 | 607.197 | 688.786 | 600.554 | 1107.57 | 90.0036
49.4486 | 39.7197 | 64.0673 | 26.4656 | 96.2485 | 11.3798 | 125.077 | 6.1709 | 158.211 | 9.9428 | 203.758 | 10.9884 | 265.85 | 10.1537 | 375.0726 | 7.9236 |  |  | 640.296 | 4.2497 | 487.813 | 403.773 | 583.434 | 607.197 | 688.786 | 600.554 | 1079.15 | 116.03
49.4981 | 49.0013 | 63.4933 | 30.4123 | 94.5316 | 13.3677 | 122.846 | 6.8953 | 155.233 | 11.1656 | 199.923 | 12.7285 | 260.846 | 11.5518 | 368.3914 | 8.9696 |  |  | 623.863 | 4.9128 | 485.38 | 502.629 | 583.434 | 607.197 | 688.786 | 600.554 | 1055.67 | 142.43
49.5476 | 65.03 | 62.9244 | 35.2987 | 92.7524 | 16.2297 | 120.534 | 7.7125 | 152.77 | 12.5264 | 195.964 | 15.1325 | 255.937 | 13.3543 | 364.0065 | 9.9031 |  |  | 607.852 | 5.7422 | 483.926 | 556.047 | 583.434 | 607.197 | 688.786 | 600.554 | 1027.54 | 179.801
49.5972 | 85.443 | 62.2983 | 43.4168 | 90.4623 | 21.1755 | 118.739 | 8.5749 | 150.796 | 13.969 | 191.7 | 18.135 | 251.623 | 15.2846 | 359.6651 | 11.0214 |  |  | 591.068 | 6.9022 | 483.442 | 606.59 | 583.434 | 607.197 | 688.786 | 600.554 | 1004.18 | 226.977
49.5972 | 123.451 | 61.7401 | 54.2091 | 89.2047 | 25.4788 | 116.855 | 9.6296 | 148.7 | 15.4382 | 187.716 | 22.7564 | 247.629 | 17.3544 | 353.9559 | 12.4889 |  |  | 578.785 | 7.9236 |  |  | 583.434 | 607.197 | 688.786 | 600.554 | 981.352 | 279.458
49.5972 | 169.839 | 61.2482 | 67.6839 | 88.2288 | 29.9895 | 115.115 | 10.814 | 146.779 | 17.4239 | 184.367 | 28.4699 | 243.698 | 20.0022 | 348.6856 | 14.2512 |  |  | 565.625 | 9.4201 |  |  | 583.434 | 607.197 | 688.786 | 600.554 | 960.958 | 339.628
49.5972 | 227.887 | 60.8209 | 88.3096 | 87.0893 | 36.7393 | 113.628 | 12.0232 | 145.028 | 19.6651 | 181.079 | 34.8428 | 238.634 | 24.1635 | 343.8381 | 15.9881 |  |  | 554.425 | 11.1322 |  |  | 583.434 | 607.197 | 688.786 | 600.554 | 939.108 | 424.899
49.6468 | 306.081 | 60.3363 | 117.196 | 86.3953 | 42.9848 | 112.048 | 13.9133 | 143.299 | 22.3281 | 178.026 | 45.8717 | 235.316 | 27.7114 | 339.3973 | 18.2077 |  |  | 542.361 | 13.3143 |  |  | 583.434 | 607.197 | 688.786 | 600.554 | 918.674 | 519.493
49.5972 | 429.17 | 60.1556 | 161.233 | 85.3648 | 52.7122 | 110.38 | 15.9721 | 141.731 | 25.9415 | 175.2 | 59.1957 | 232.045 | 32.0676 | 335.0138 | 20.9438 |  |  | 531.09 | 16.3274 |  |  | 583.434 | 607.197 | 688.786 | 600.554 | 903.188 | 596.962
49.5972 | 520.533 | 59.8555 | 210.366 | 84.6 | 67.1446 | 109.063 | 18.706 | 140.18 | 29.1614 | 172.592 | 75.5541 | 228.819 | 37.0344 | 329.375 | 24.4553 |  |  | 522.66 | 18.9508 |  |  | 583.434 | 607.197 | 688.786 | 600.554 | 901.384 | 613.299
49.5972 | 577.006 | 59.8555 | 270.386 | 83.6745 | 85.8713 | 107.655 | 21.9078 | 138.508 | 34.2897 | 170.363 | 94.9025 | 225.638 | 42.8132 | 325.1361 | 28.1584 |  |  | 514.364 | 22.6655
49.5972 | 602.961 | 59.8555 | 332.57 | 83.0908 | 104.883 | 106.584 | 25.3263 | 136.856 | 40.7659 | 167.994 | 124.194 | 222.946 | 48.4168 | 321.5928 | 33.2098 |  |  | 505.188 | 27.1899
|  | 59.9154 | 414.823 | 82.5937 | 126.576 | 105.629 | 29.5725 | 135.088 | 53.4554 | 166.157 | 159.309 | 220.287 | 56.2524 | 317.1285 | 39.1283 |  |  | 498.165 | 31.8121
|  | 59.9154 | 491.201 | 82.1818 | 155.066 | 104.473 | 35.7964 | 134.012 | 64.0618 | 164.833 | 207.027 | 217.442 | 64.4473 | 313.3576 | 46.892 |  |  | 489.278 | 38.1241
|  | 59.9154 | 566.147 | 81.6902 | 201.512 | 103.641 | 42.7277 | 132.944 | 76.3898 | 163.683 | 258.747 | 214.633 | 76.6193 | 310.5598 | 57.2741 |  |  | 482.476 | 45.7342
|  | 59.9154 | 608.413 | 81.2827 | 255.66 | 102.815 | 51.8756 | 131.753 | 98.0865 | 162.541 | 325.985 | 212.285 | 88.7523 | 308.4019 | 67.4137 |  |  | 475.293 | 53.8848
|  |  |  | 80.7158 | 336.249 | 102.302 | 61.1206 | 130.965 | 115.451 | 161.407 | 415.238 | 209.963 | 101.58 | 305.9524 | 83.2501 |  |  | 468.217 | 64.7056
|  |  |  | 80.3132 | 422.358 | 101.487 | 74.8772 | 129.921 | 141.012 | 160.442 | 498.624 | 207.458 | 122.101 | 303.8217 | 104.151 |  |  | 460.324 | 85.443
|  |  |  | 79.9126 | 513.81 | 101.183 | 86.9949 | 129.403 | 170.69 | 159.961 | 559.393 | 205.394 | 146.767 | 302.9171 | 127.593 |  |  | 453.471 | 110.15
|  |  |  | 79.753 | 578.161 | 100.678 | 105.937 | 129.015 | 216.34 | 159.322 | 605.984 | 203.35 | 178.19 | 301.1073 | 167.645 |  |  | 447.614 | 139.191
|  |  |  | 79.5936 | 609.021 | 100.276 | 127.466 | 128.886 | 278.621 |  |  | 201.327 | 209.108 | 300.8075 | 205.172 |  |  | 441.391 | 185.091
[6 empty] | 99.9763 | 173.79 | 128.5 | 359.549 |  |  | 200.123 | 251.602 | 300.8099 | 271.47 |  |  | 436.999 | 232.258
[6 empty] | 99.6769 | 223.598 | 128.5 | 461.21 |  |  | 198.926 | 299.122 | 301.1126 | 341.672 |  |  | 432.651 | 300.922
[6 empty] | 99.4777 | 282.549 | 128.5 | 569.554 |  |  | 197.933 | 362.075 | 301.1134 | 418.573 |  |  | 428.775 | 379.499
[6 empty] | 99.0806 | 347.878 | 128.372 | 601.757 |  |  | 196.749 | 446.684 | 301.4152 | 528.928 |  |  | 425.784 | 486.313
[6 empty] | 98.6851 | 424.475 |  |  |  |  | 195.964 | 553.827 | 301.1143 | 577.584 |  |  | 423.66 | 570.124
[6 empty] | 98.3895 | 488.262 |  |  |  |  | 195.182 | 601.155 | 301 | 604.773 |  |  | 421.969 | 607.197
[6 empty] | 98.0947 | 568.984
[6 empty] | 97.9967 | 602.359