## 685-9
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Tap Interrupter Speed (TCC 685-9) | [9 empty] | Tap Interrupter Speed (TCC 685-9)
Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Curves are plotted to maximum test points. | [8 empty] | Tolerance: | Curves are plotted to maximum test points.
| Maximum variations are plu 10% in terms of current, plus 20% in terms of time, | [9 empty] | Maximum variations are plu 10% in terms of current, plus 20% in terms of time,
| or plus 6 milliseconds (60-Hz), plus 10 milliseconds (50-Hz), whichever is greater. | [9 empty] | or plus 6 milliseconds (60-Hz), plus 10 milliseconds (50-Hz), whichever is greater.
50 A |  | 65 A |  | 80 A |  | 100 A |  | 150 A |  | 200 A |  | 250 A |  | 300 A |  | 350 A |  | 400 A
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
1422.396 | 0.01 | 1791.377 | 0.0102 | 2253.835 | 0.0101 | 2799.797 | 0.0101 | 4078.356 | 0.01 | 5556.466 | 0.0101 | 6866.981 | 0.0102 | 8637.286 | 0.0101 | 10236.008 | 0.0101 | 11845.158 | 0.01
1350.266 | 0.0106 | 1421.761 | 0.0133 | 1974.707 | 0.0119 | 2515.145 | 0.0114 | 3584.398 | 0.0117 | 4965.927 | 0.0115 | 6143.693 | 0.0116 | 7922.73 | 0.0111 | 9350.288 | 0.0112 | 10707.881 | 0.0113
1269.842 | 0.0113 | 1198.634 | 0.0161 | 1715.799 | 0.0141 | 2212.88 | 0.0131 | 3170.008 | 0.0134 | 4428.925 | 0.0132 | 5311.115 | 0.0137 | 7274.854 | 0.0124 | 8612.587 | 0.0124 | 9649.624 | 0.0127
1269.842 | 0.0113 | 1117.886 | 0.0177 | 1492.389 | 0.0165 | 1940.871 | 0.0152 | 2762.956 | 0.0159 | 3925.413 | 0.0152 | 4615.307 | 0.0162 | 6522.01 | 0.014 | 7818.389 | 0.0138 | 8614.893 | 0.0146
1183.074 | 0.0121 | 1007.372 | 0.0202 | 1364.582 | 0.0184 | 1712.962 | 0.0177 | 2515.816 | 0.0178 | 3574.539 | 0.017 | 4142.09 | 0.0185 | 5914.375 | 0.0157 | 7112.209 | 0.0155 | 7731.238 | 0.0167
1098.799 | 0.0131 | 899.32 | 0.0234 | 1249.02 | 0.0204 | 1519.705 | 0.0204 | 2170.056 | 0.0215 | 3168.16 | 0.0197 | 3690.424 | 0.0214 | 5363.351 | 0.0176 | 6564.728 | 0.0171 | 7010.799 | 0.0189
1045.252 | 0.014 | 788.774 | 0.0278 | 1123.189 | 0.0234 | 1402.651 | 0.0226 | 1925.18 | 0.025 | 2784.706 | 0.0232 | 3257.371 | 0.0249 | 4894.12 | 0.0197 | 5971.782 | 0.0191 | 6066.652 | 0.0227
988.124 | 0.0149 | 715.25 | 0.0317 | 1037.748 | 0.0259 | 1290.576 | 0.0251 | 1706.16 | 0.0298 | 2387.303 | 0.0285 | 2957.027 | 0.0285 | 4419.719 | 0.0224 | 5494.913 | 0.0213 | 5348.911 | 0.0268
932.176 | 0.0158 | 626.026 | 0.0379 | 941.006 | 0.0294 | 1141.403 | 0.0295 | 1534.259 | 0.0349 | 2189.804 | 0.0319 | 2709.624 | 0.0319 | 4020.477 | 0.0252 | 4967.494 | 0.024 | 4730.832 | 0.0314
877.567 | 0.0168 | 557.135 | 0.0449 | 849.737 | 0.0338 | 1039.327 | 0.034 | 1389.769 | 0.0407 | 2027.539 | 0.0352 | 2477.76 | 0.0364 | 3645.902 | 0.0287 | 4618.619 | 0.0265 | 4227.941 | 0.0367
833.065 | 0.018 | 497.375 | 0.0531 | 771.325 | 0.0389 | 920.152 | 0.0398 | 1261.511 | 0.0471 | 1854.007 | 0.04 | 2232.982 | 0.0421 | 3295.921 | 0.0329 | 4240.972 | 0.0298 | 3790.322 | 0.0431
767.307 | 0.0197 | 446.343 | 0.063 | 681.451 | 0.047 | 829.187 | 0.0471 | 1149.868 | 0.054 | 1672.552 | 0.0464 | 2018.674 | 0.0486 | 3007.567 | 0.0372 | 3947.226 | 0.0329 | 3447.866 | 0.0496
714.877 | 0.0216 | 400.963 | 0.0748 | 610.253 | 0.056 | 747.214 | 0.0557 | 1038.33 | 0.0632 | 1519.885 | 0.0537 | 1789.222 | 0.0577 | 2767.377 | 0.0422 | 3628.249 | 0.0371 | 3090.99 | 0.058
648.923 | 0.0242 | 351.311 | 0.0929 | 552.788 | 0.0657 | 672.644 | 0.0654 | 939.566 | 0.0744 | 1354.119 | 0.0639 | 1610.788 | 0.0683 | 2475.836 | 0.0496 | 3391.024 | 0.0407 | 2800.039 | 0.0666
609.637 | 0.0263 | 318.896 | 0.1088 | 493.489 | 0.0789 | 599.87 | 0.0779 | 851.081 | 0.0871 | 1226.683 | 0.0741 | 1427.698 | 0.0819 | 2226.561 | 0.0574 | 3123.486 | 0.046 | 2533.837 | 0.0791
556.859 | 0.0297 | 286.474 | 0.1296 | 449.82 | 0.0921 | 538.882 | 0.0928 | 767.726 | 0.1024 | 1120.528 | 0.0855 | 1281.313 | 0.0979 | 1996.143 | 0.0683 | 2874.064 | 0.0524 | 2290.558 | 0.0924
504.432 | 0.0342 | 263.036 | 0.1533 | 405.768 | 0.1088 | 485.103 | 0.1106 | 686.076 | 0.1239 | 1023.559 | 0.0997 | 1177.78 | 0.112 | 1831.004 | 0.0778 | 2639.063 | 0.0592 | 2077.112 | 0.1059
468.499 | 0.038 | 238.021 | 0.1883 | 365.27 | 0.1285 | 440.802 | 0.1297 | 610.561 | 0.1511 | 909.083 | 0.121 | 1090.524 | 0.1287 | 1679.527 | 0.0891 | 2395.705 | 0.0682 | 1917.172 | 0.1222
440.136 | 0.0419 | 216.961 | 0.2258 | 332.947 | 0.1514 | 401.381 | 0.1549 | 554.214 | 0.1801 | 846.11 | 0.1377 | 985.863 | 0.153 | 1535.78 | 0.1027 | 2177.052 | 0.0787 | 1742.142 | 0.1427
400.362 | 0.0482 | 198.589 | 0.2715 | 304.751 | 0.1789 | 363.967 | 0.1848 | 502.021 | 0.2168 | 765.686 | 0.1632 | 913.775 | 0.1795 | 1386.912 | 0.1213 | 2003.206 | 0.0894 | 1583.091 | 0.1702
380.059 | 0.0531 | 184.826 | 0.3182 | 278.362 | 0.2094 | 332.454 | 0.2211 | 459.502 | 0.2594 | 703.804 | 0.1927 | 826.936 | 0.2156 | 1270.851 | 0.1402 | 1839.412 | 0.1021 | 1434.076 | 0.2026
356.679 | 0.0587 | 174.178 | 0.3617 | 253.73 | 0.2551 | 308.448 | 0.2588 | 419.709 | 0.3124 | 650.975 | 0.2251 | 761.701 | 0.2532 | 1169.359 | 0.1614 | 1681.997 | 0.1194 | 1315.413 | 0.2409
326.14 | 0.0679 | 160.595 | 0.442 | 232.969 | 0.302 | 287.669 | 0.3001 | 385.765 | 0.3761 | 592.787 | 0.2733 | 701.612 | 0.3035 | 1084.965 | 0.1868 | 1525.306 | 0.1408 | 1200.306 | 0.2898
297.285 | 0.0782 | 149.62 | 0.525 | 216.145 | 0.3539 | 263.859 | 0.3667 | 358.65 | 0.4467 | 533.658 | 0.3456 | 642.911 | 0.3673 | 1003.524 | 0.2155 | 1404.965 | 0.1619 | 1117.143 | 0.3388
274.675 | 0.0883 | 138.672 | 0.64 | 195.791 | 0.4471 | 243.789 | 0.4433 | 332.401 | 0.5334 | 498.244 | 0.408 | 608.427 | 0.4233 | 939.858 | 0.2486 | 1298.164 | 0.1899 | 1038.66 | 0.4021
256.173 | 0.1 | 128.258 | 0.7795 | 177.354 | 0.549 | 221.525 | 0.5439 | 306.155 | 0.649 | 467.606 | 0.4846 | 568.059 | 0.5059 | 872.027 | 0.2922 | 1194.501 | 0.2218 | 961.68 | 0.4821
239.415 | 0.1127 | 118.873 | 0.9385 | 162.673 | 0.6694 | 204.037 | 0.6631 | 286.718 | 0.7701 | 438.852 | 0.562 | 521.616 | 0.6207 | 797.392 | 0.3526 | 1103.699 | 0.2629 | 895.05 | 0.5738
221.437 | 0.1275 | 111.096 | 1.1395 | 150.298 | 0.8085 | 189.896 | 0.791 | 266.01 | 0.9224 | 408.028 | 0.6613 | 476.981 | 0.7678 | 739.074 | 0.4205 | 1026.184 | 0.3017 | 825.271 | 0.6909
209.116 | 0.1427 | 103.181 | 1.362 | 142.082 | 0.9654 | 176.001 | 0.9593 | 250.422 | 1.0934 | 381.347 | 0.788 | 439.353 | 0.9458 | 684.309 | 0.5084 | 956.101 | 0.3588 | 767.294 | 0.8276
192.81 | 0.1643 | 97.237 | 1.6111 | 132.372 | 1.1806 | 166.381 | 1.1033 | 234.279 | 1.3069 | 356.411 | 0.935 | 408.499 | 1.1471 | 640.228 | 0.592 | 906.698 | 0.4096 | 723.858 | 0.9759
177.776 | 0.1919 | 91.065 | 1.9378 | 123.325 | 1.4852 | 154.688 | 1.3339 | 221.471 | 1.5786 | 329.315 | 1.1436 | 385.785 | 1.3483 | 603.993 | 0.6801 | 849.18 | 0.4834 | 674.407 | 1.1665
167.187 | 0.2182 | 84.842 | 2.3923 | 115.376 | 1.7976 | 145.625 | 1.6128 | 209.799 | 1.877 | 306.822 | 1.4074 | 359.441 | 1.6801 | 554.602 | 0.8344 | 787.9 | 0.5712 | 642.885 | 1.3669
155.763 | 0.2504 | 80.623 | 2.8446 | 108.842 | 2.1825 | 136.24 | 1.9973 | 198.95 | 2.2111 | 290.361 | 1.6718 | 339.101 | 1.9852 | 519.416 | 1.0099 | 744.085 | 0.6596 | 606.492 | 1.6407
143.767 | 0.2952 | 77.014 | 3.3859 | 103.214 | 2.4813 | 128.793 | 2.4581 | 190.636 | 2.6045 | 271.657 | 2.0298 | 322.922 | 2.3677 | 484.443 | 1.2222 | 690.389 | 0.7917 | 573.948 | 1.9489
135.204 | 0.3427 | 73.873 | 3.9967 | 99.417 | 2.8416 | 121.627 | 2.9689 | 181.721 | 3.0905 | 258.156 | 2.4516 | 306.557 | 2.9229 | 456.549 | 1.4808 | 654.035 | 0.8982 | 547.691 | 2.2981
124.921 | 0.4118 | 72.05 | 4.492 | 95.263 | 3.3194 | 116.545 | 3.5709 | 176.316 | 3.5027 | 245.836 | 2.9212 | 293.147 | 3.5448 | 430.262 | 1.7754 | 620.24 | 1.0275 | 518.303 | 2.8018
118.34 | 0.4726 | 70.566 | 5.139 | 90.903 | 4.0555 | 113.197 | 4.304 | 171.786 | 4.0577 | 236.799 | 3.4555 | 282.961 | 4.2633 | 411.01 | 2.0956 | 584.531 | 1.223 | 497.689 | 3.3074
112.573 | 0.5284 | 69.256 | 6.0788 | 87.651 | 5.012 | 110.749 | 4.9807 | 166.677 | 4.8451 | 228.331 | 4.1606 | 274.553 | 5.0007 | 388.152 | 2.5258 | 549.162 | 1.4786 | 486.425 | 3.768
104.881 | 0.6238 | 67.758 | 7.45 | 85.133 | 6.0346 | 107.905 | 6.022 | 162.394 | 5.6895 | 219.48 | 5.2122 | 267.784 | 5.8596 | 372.33 | 3.0063 | 511.125 | 1.8063 | 470.494 | 4.6374
98.02 | 0.7219 | 67.057 | 8.8862 | 83.465 | 7.1084 | 104.914 | 7.1979 | 159.048 | 6.7864 | 213.845 | 6.1847 | 261.182 | 7.1584 | 359.764 | 3.6083 | 488.257 | 2.1188 | 457.935 | 5.6776
92.277 | 0.8433 | 66.501 | 10.4457 | 82.429 | 8.4523 | 103.074 | 8.6846 | 154.8 | 8.3871 | 208.138 | 7.9277 | 255.804 | 8.6724 | 347.26 | 4.2591 | 464.475 | 2.5377 | 443.398 | 7.1648
87.053 | 0.9841 | 66.293 | 12.2532 | 81.321 | 10.198 | 101.161 | 10.3697 | 151.768 | 10.0775 | 203.852 | 9.8694 | 251.582 | 10.2898 | 336.939 | 5.1012 | 443.694 | 3.0362 | 434.718 | 8.5105
82.552 | 1.1246 | 65.743 | 15.5756 | 80.647 | 12.2532 | 100.009 | 11.9877 | 150.352 | 12.1212 | 200.695 | 11.9954 | 248.461 | 12.6232 | 327.947 | 6.3304 | 423.843 | 3.6862 | 427.985 | 10.067
78.04 | 1.3138 | 66.018 | 20.5779 | 80.731 | 14.3734 | 99.905 | 14.1799 | 149.416 | 14.4883 | 199.862 | 13.6235 | 247.43 | 15.5991 | 318.2 | 7.7986 | 412.533 | 4.217 | 423.554 | 11.9829
73.775 | 1.5622 | 65.949 | 26.1574 | 80.395 | 16.9135 | 99.593 | 18.0811 | 148.64 | 17.4811 | 198.825 | 16.5927 | 246.659 | 18.9576 | 312.622 | 9.3993 | 401.524 | 5.0402 | 421.795 | 14.4883
69.743 | 1.8731 | 65.88 | 30.7478 | 80.144 | 19.9855 | 99.697 | 22.9358 | 149.105 | 20.8951 | 199.862 | 20.7863 | 250.017 | 21.3283 | 307.141 | 11.4115 | 390.81 | 5.7599 | 421.356 | 17.8125
66.275 | 2.2273 | 65.812 | 40.3273 | 80.311 | 25.1671 | 100.009 | 29.0334 | 149.416 | 24.8976 | 199.654 | 27.6353 | 250.277 | 28.0288 | 303.331 | 13.9414 | 381.57 | 6.942 | 420.918 | 22.572
66 | 2.2319 | 65.743 | 50.5714 | 79.895 | 30.9731 | 99.697 | 37.3705 | 149.572 | 31.6822 | 199.654 | 35.056 | 250.277 | 37.7678 | 303.015 | 17.5369 | 374.102 | 8.2283 | 419.169 | 30.2608
63.374 | 2.6264 | 65.949 | 63.1537 | 79.811 | 41.006 | 100.009 | 47.7517 | 149.572 | 39.442 | 199.239 | 45.4543 | 249.497 | 50.8908 | 301.757 | 22.8798 | 367.544 | 9.8551 | 420.48 | 40.6959
61.235 | 3.0016 | 65.812 | 78.1295 | 79.563 | 53.6695 | 99.905 | 61.9143 | 149.26 | 47.3418 | 199.654 | 60.8107 | 249.238 | 65.7721 | 301.129 | 28.601 | 361.477 | 11.9771 | 419.169 | 53.3761
59.106 | 3.4411 | 65.743 | 97.2634 | 80.395 | 69.1531 | 100.113 | 79.4444 | 149.416 | 58.0825 | 199.239 | 80.5107 | 249.497 | 84.1233 | 301.129 | 36.7356 | 358.482 | 14.375 | 420.918 | 66.588
57.888 | 3.9533 | 65.88 | 124.2824 | 80.228 | 85.7302 | 100.113 | 100.1461 | 149.105 | 69.9343 | 199.032 | 103.8487 | 248.72 | 103.1992 | 300.816 | 47.6288 | 359.602 | 17.5068 | 418.298 | 87.5182
56.401 | 4.5369 | 65.88 | 156.3416 | 80.311 | 110.4634 | 100.009 | 125.7167 | 149.727 | 86.5197 | 199.032 | 138.2102 | 248.72 | 130.8964 | 300.191 | 62.5297 | 358.855 | 21.8612 | 420.043 | 109.6378
55.01 | 5.2833 | 65.812 | 200.8166 | 80.395 | 140.5615 | 99.593 | 156.9953 | 150.196 | 108.0481 | 199.239 | 180.8965 | 250.017 | 165.8542 | 299.879 | 79.398 | 358.109 | 29.122 | 420.918 | 137.3478
54.045 | 5.9381 | 65.743 | 247.1445 | 79.978 | 179.421 | 99.697 | 194.224 | 149.727 | 136.4908 | 199.446 | 233.8211 | 250.017 | 203.6758 | 299.567 | 99.1484 | 359.976 | 40.5312 | 420.918 | 169.0368
53.374 | 6.7652 | 65.812 | 301.318 | 79.811 | 227.8323 | 99.593 | 237.0446 | 149.572 | 171.7027 | 199.446 | 300.0307 | 250.017 | 258.6091 | 299.879 | 130.7118 | 359.602 | 51.8952 | 419.169 | 212.4232
52.111 | 8.2828 | 66.087 | 381.0263 | 79.811 | 289.0043 | 99.386 | 304.1601 | 149.727 | 219.6342 | 199.654 | 381.3907 | 249.757 | 336.3287 | 300.191 | 165.4547 | 362.23 | 64.0637 | 420.043 | 273.9991
51.465 | 9.8386 | 66.087 | 464.5464 | 79.314 | 371.2183 | 99.593 | 375.1109 | 149.727 | 277.4508 | 199.446 | 469.3854 | 249.757 | 406.6155 | 300.191 | 205.5373 | 360.351 | 79.9981 | 420.918 | 346.8497
50.773 | 11.8709 | 66.018 | 538.1522 | 79.232 | 456.8575 | 99.49 | 454.0071 | 149.105 | 356.3863 | 199.862 | 544.3327 | 250.798 | 503.5235 | 298.944 | 261.5289 | 361.102 | 98.9626 | 419.606 | 419.8091
50.3 | 14.1154 | 66.155 | 588.6606 | 79.232 | 527.0414 | 100.009 | 529.245 | 149.883 | 453.9746 | 200.278 | 601.6701 | 251.844 | 600.5548 | 298.944 | 330.3529 | 361.854 | 122.4228 | 417.863 | 507.0563
50.091 | 16.9072 |  |  | 79.811 | 591.7389 | 100.113 | 588.0469 | 150.509 | 530.3198 |  |  |  |  | 299.567 | 412.9593 | 360.351 | 153.9927 | 419.169 | 597.9159
50.3 | 19.8953 | [6 empty] | 150.196 | 589.8618 |  |  |  |  | 299.879 | 502.9361 | 361.477 | 195.3264
50.143 | 24.8198 | [12 empty] | 299.879 | 591.1783 | 363.363 | 255.8949
50.038 | 29.7599 | [14 empty] | 362.607 | 324.5805
50.143 | 34.7284 | [14 empty] | 363.363 | 397.7752
49.934 | 39.7311 | [14 empty] | 362.985 | 502.9674
49.986 | 49.9288 | [14 empty] | 364.119 | 597.404
49.934 | 59.8041
49.779 | 69.9343
49.779 | 79.9249
49.779 | 99.2931
49.572 | 120.4303
49.675 | 148.9912
49.624 | 188.8017
49.572 | 188.6048
49.675 | 296.917
49.727 | 394.3375
49.934 | 497.6237
49.52 | 592.9466
49.727 | 221.2439
49.624 | 241.5064