## 692-9-C4
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Long-Time Inverse I.E.C. (C4) (TCC 692-9-C4) | [9 empty] | Long-Time Inverse I.E.C. (C4) (TCC 692-9-C4) | [9 empty] | Long-Time Inverse I.E.C. (C4) (TCC 692-9-C4)
Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
| current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5
| cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between
| 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting.
| Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup
| current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.05 |  | Time Dial = 0.1 |  | Time Dial = 0.2 |  | Time Dial = 0.3 |  | Time Dial = 0.4 |  | Time Dial = 0.5 |  | Time Dial = 0.6 |  | Time Dial = 0.7 |  | Time Dial = 0.8 |  | Time Dial = 0.9 |  | Time Dial = 1.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 12 | 1.5 | 24 | 1.5 | 48 | 1.5 | 72 | 1.5 | 96 | 1.5 | 120 | 1.5 | 144 | 1.5 | 168 | 1.5 | 192 | 1.5 | 216 | 1.5 | 240
1.6 | 10 | 1.6 | 20 | 1.6 | 40 | 1.6 | 60 | 1.6 | 80 | 1.6 | 100 | 1.6 | 120 | 1.6 | 140 | 1.6 | 160 | 1.6 | 180 | 1.6 | 200
1.7 | 8.5714 | 1.7 | 17.1429 | 1.7 | 34.2857 | 1.7 | 51.4286 | 1.7 | 68.5714 | 1.7 | 85.7143 | 1.7 | 102.8571 | 1.7 | 120 | 1.7 | 137.1429 | 1.7 | 154.2857 | 1.7 | 171.4286
1.8 | 7.5 | 1.8 | 15 | 1.8 | 30 | 1.8 | 45 | 1.8 | 60 | 1.8 | 75 | 1.8 | 90 | 1.8 | 105 | 1.8 | 120 | 1.8 | 135 | 1.8 | 150
1.9 | 6.6667 | 1.9 | 13.3333 | 1.9 | 26.6667 | 1.9 | 40 | 1.9 | 53.3333 | 1.9 | 66.6667 | 1.9 | 80 | 1.9 | 93.3333 | 1.9 | 106.6667 | 1.9 | 120 | 1.9 | 133.3333
2 | 6 | 2 | 12 | 2 | 24 | 2 | 36 | 2 | 48 | 2 | 60 | 2 | 72 | 2 | 84 | 2 | 96 | 2 | 108 | 2 | 120
2.1 | 5.4545 | 2.1 | 10.9091 | 2.1 | 21.8182 | 2.1 | 32.7273 | 2.1 | 43.6364 | 2.1 | 54.5455 | 2.1 | 65.4545 | 2.1 | 76.3636 | 2.1 | 87.2727 | 2.1 | 98.1818 | 2.1 | 109.0909
2.2 | 5 | 2.2 | 10 | 2.2 | 20 | 2.2 | 30 | 2.2 | 40 | 2.2 | 50 | 2.2 | 60 | 2.2 | 70 | 2.2 | 80 | 2.2 | 90 | 2.2 | 100
2.3 | 4.6154 | 2.3 | 9.2308 | 2.3 | 18.4615 | 2.3 | 27.6923 | 2.3 | 36.9231 | 2.3 | 46.1538 | 2.3 | 55.3846 | 2.3 | 64.6154 | 2.3 | 73.8462 | 2.3 | 83.0769 | 2.3 | 92.3077
2.4 | 4.2857 | 2.4 | 8.5714 | 2.4 | 17.1429 | 2.4 | 25.7143 | 2.4 | 34.2857 | 2.4 | 42.8571 | 2.4 | 51.4286 | 2.4 | 60 | 2.4 | 68.5714 | 2.4 | 77.1429 | 2.4 | 85.7143
2.5 | 4 | 2.5 | 8 | 2.5 | 16 | 2.5 | 24 | 2.5 | 32 | 2.5 | 40 | 2.5 | 48 | 2.5 | 56 | 2.5 | 64 | 2.5 | 72 | 2.5 | 80
2.6 | 3.75 | 2.6 | 7.5 | 2.6 | 15 | 2.6 | 22.5 | 2.6 | 30 | 2.6 | 37.5 | 2.6 | 45 | 2.6 | 52.5 | 2.6 | 60 | 2.6 | 67.5 | 2.6 | 75
2.7 | 3.5294 | 2.7 | 7.0588 | 2.7 | 14.1176 | 2.7 | 21.1765 | 2.7 | 28.2353 | 2.7 | 35.2941 | 2.7 | 42.3529 | 2.7 | 49.4118 | 2.7 | 56.4706 | 2.7 | 63.5294 | 2.7 | 70.5882
2.8 | 3.3333 | 2.8 | 6.6667 | 2.8 | 13.3333 | 2.8 | 20 | 2.8 | 26.6667 | 2.8 | 33.3333 | 2.8 | 40 | 2.8 | 46.6667 | 2.8 | 53.3333 | 2.8 | 60 | 2.8 | 66.6667
2.9 | 3.1579 | 2.9 | 6.3158 | 2.9 | 12.6316 | 2.9 | 18.9474 | 2.9 | 25.2632 | 2.9 | 31.5789 | 2.9 | 37.8947 | 2.9 | 44.2105 | 2.9 | 50.5263 | 2.9 | 56.8421 | 2.9 | 63.1579
3 | 3 | 3 | 6 | 3 | 12 | 3 | 18 | 3 | 24 | 3 | 30 | 3 | 36 | 3 | 42 | 3 | 48 | 3 | 54 | 3 | 60
3.1 | 2.8571 | 3.1 | 5.7143 | 3.1 | 11.4286 | 3.1 | 17.1429 | 3.1 | 22.8571 | 3.1 | 28.5714 | 3.1 | 34.2857 | 3.1 | 40 | 3.1 | 45.7143 | 3.1 | 51.4286 | 3.1 | 57.1429
3.2 | 2.7273 | 3.2 | 5.4545 | 3.2 | 10.9091 | 3.2 | 16.3636 | 3.2 | 21.8182 | 3.2 | 27.2727 | 3.2 | 32.7273 | 3.2 | 38.1818 | 3.2 | 43.6364 | 3.2 | 49.0909 | 3.2 | 54.5455
3.3 | 2.6087 | 3.3 | 5.2174 | 3.3 | 10.4348 | 3.3 | 15.6522 | 3.3 | 20.8696 | 3.3 | 26.087 | 3.3 | 31.3043 | 3.3 | 36.5217 | 3.3 | 41.7391 | 3.3 | 46.9565 | 3.3 | 52.1739
3.4 | 2.5 | 3.4 | 5 | 3.4 | 10 | 3.4 | 15 | 3.4 | 20 | 3.4 | 25 | 3.4 | 30 | 3.4 | 35 | 3.4 | 40 | 3.4 | 45 | 3.4 | 50
3.5 | 2.4 | 3.5 | 4.8 | 3.5 | 9.6 | 3.5 | 14.4 | 3.5 | 19.2 | 3.5 | 24 | 3.5 | 28.8 | 3.5 | 33.6 | 3.5 | 38.4 | 3.5 | 43.2 | 3.5 | 48
3.6 | 2.3077 | 3.6 | 4.6154 | 3.6 | 9.2308 | 3.6 | 13.8462 | 3.6 | 18.4615 | 3.6 | 23.0769 | 3.6 | 27.6923 | 3.6 | 32.3077 | 3.6 | 36.9231 | 3.6 | 41.5385 | 3.6 | 46.1538
3.7 | 2.2222 | 3.7 | 4.4444 | 3.7 | 8.8889 | 3.7 | 13.3333 | 3.7 | 17.7778 | 3.7 | 22.2222 | 3.7 | 26.6667 | 3.7 | 31.1111 | 3.7 | 35.5556 | 3.7 | 40 | 3.7 | 44.4444
3.8 | 2.1429 | 3.8 | 4.2857 | 3.8 | 8.5714 | 3.8 | 12.8571 | 3.8 | 17.1429 | 3.8 | 21.4286 | 3.8 | 25.7143 | 3.8 | 30 | 3.8 | 34.2857 | 3.8 | 38.5714 | 3.8 | 42.8571
3.9 | 2.069 | 3.9 | 4.1379 | 3.9 | 8.2759 | 3.9 | 12.4138 | 3.9 | 16.5517 | 3.9 | 20.6897 | 3.9 | 24.8276 | 3.9 | 28.9655 | 3.9 | 33.1034 | 3.9 | 37.2414 | 3.9 | 41.3793
4 | 2 | 4 | 4 | 4 | 8 | 4 | 12 | 4 | 16 | 4 | 20 | 4 | 24 | 4 | 28 | 4 | 32 | 4 | 36 | 4 | 40
4.1 | 1.9355 | 4.1 | 3.871 | 4.1 | 7.7419 | 4.1 | 11.6129 | 4.1 | 15.4839 | 4.1 | 19.3548 | 4.1 | 23.2258 | 4.1 | 27.0968 | 4.1 | 30.9677 | 4.1 | 34.8387 | 4.1 | 38.7097
4.2 | 1.875 | 4.2 | 3.75 | 4.2 | 7.5 | 4.2 | 11.25 | 4.2 | 15 | 4.2 | 18.75 | 4.2 | 22.5 | 4.2 | 26.25 | 4.2 | 30 | 4.2 | 33.75 | 4.2 | 37.5
4.3 | 1.8182 | 4.3 | 3.6364 | 4.3 | 7.2727 | 4.3 | 10.9091 | 4.3 | 14.5455 | 4.3 | 18.1818 | 4.3 | 21.8182 | 4.3 | 25.4545 | 4.3 | 29.0909 | 4.3 | 32.7273 | 4.3 | 36.3636
4.4 | 1.7647 | 4.4 | 3.5294 | 4.4 | 7.0588 | 4.4 | 10.5882 | 4.4 | 14.1176 | 4.4 | 17.6471 | 4.4 | 21.1765 | 4.4 | 24.7059 | 4.4 | 28.2353 | 4.4 | 31.7647 | 4.4 | 35.2941
4.5 | 1.7143 | 4.5 | 3.4286 | 4.5 | 6.8571 | 4.5 | 10.2857 | 4.5 | 13.7143 | 4.5 | 17.1429 | 4.5 | 20.5714 | 4.5 | 24 | 4.5 | 27.4286 | 4.5 | 30.8571 | 4.5 | 34.2857
4.6 | 1.6667 | 4.6 | 3.3333 | 4.6 | 6.6667 | 4.6 | 10 | 4.6 | 13.3333 | 4.6 | 16.6667 | 4.6 | 20 | 4.6 | 23.3333 | 4.6 | 26.6667 | 4.6 | 30 | 4.6 | 33.3333
4.7 | 1.6216 | 4.7 | 3.2432 | 4.7 | 6.4865 | 4.7 | 9.7297 | 4.7 | 12.973 | 4.7 | 16.2162 | 4.7 | 19.4595 | 4.7 | 22.7027 | 4.7 | 25.9459 | 4.7 | 29.1892 | 4.7 | 32.4324
4.8 | 1.5789 | 4.8 | 3.1579 | 4.8 | 6.3158 | 4.8 | 9.4737 | 4.8 | 12.6316 | 4.8 | 15.7895 | 4.8 | 18.9474 | 4.8 | 22.1053 | 4.8 | 25.2632 | 4.8 | 28.4211 | 4.8 | 31.5789
4.9 | 1.5385 | 4.9 | 3.0769 | 4.9 | 6.1538 | 4.9 | 9.2308 | 4.9 | 12.3077 | 4.9 | 15.3846 | 4.9 | 18.4615 | 4.9 | 21.5385 | 4.9 | 24.6154 | 4.9 | 27.6923 | 4.9 | 30.7692
5 | 1.5 | 5 | 3 | 5 | 6 | 5 | 9 | 5 | 12 | 5 | 15 | 5 | 18 | 5 | 21 | 5 | 24 | 5 | 27 | 5 | 30
5.1 | 1.4634 | 5.1 | 2.9268 | 5.1 | 5.8537 | 5.1 | 8.7805 | 5.1 | 11.7073 | 5.1 | 14.6341 | 5.1 | 17.561 | 5.1 | 20.4878 | 5.1 | 23.4146 | 5.1 | 26.3415 | 5.1 | 29.2683
5.2 | 1.4286 | 5.2 | 2.8571 | 5.2 | 5.7143 | 5.2 | 8.5714 | 5.2 | 11.4286 | 5.2 | 14.2857 | 5.2 | 17.1429 | 5.2 | 20 | 5.2 | 22.8571 | 5.2 | 25.7143 | 5.2 | 28.5714
5.3 | 1.3953 | 5.3 | 2.7907 | 5.3 | 5.5814 | 5.3 | 8.3721 | 5.3 | 11.1628 | 5.3 | 13.9535 | 5.3 | 16.7442 | 5.3 | 19.5349 | 5.3 | 22.3256 | 5.3 | 25.1163 | 5.3 | 27.907
5.4 | 1.3636 | 5.4 | 2.7273 | 5.4 | 5.4545 | 5.4 | 8.1818 | 5.4 | 10.9091 | 5.4 | 13.6364 | 5.4 | 16.3636 | 5.4 | 19.0909 | 5.4 | 21.8182 | 5.4 | 24.5455 | 5.4 | 27.2727
5.5 | 1.3333 | 5.5 | 2.6667 | 5.5 | 5.3333 | 5.5 | 8 | 5.5 | 10.6667 | 5.5 | 13.3333 | 5.5 | 16 | 5.5 | 18.6667 | 5.5 | 21.3333 | 5.5 | 24 | 5.5 | 26.6667
5.6 | 1.3043 | 5.6 | 2.6087 | 5.6 | 5.2174 | 5.6 | 7.8261 | 5.6 | 10.4348 | 5.6 | 13.0435 | 5.6 | 15.6522 | 5.6 | 18.2609 | 5.6 | 20.8696 | 5.6 | 23.4783 | 5.6 | 26.087
5.7 | 1.2766 | 5.7 | 2.5532 | 5.7 | 5.1064 | 5.7 | 7.6596 | 5.7 | 10.2128 | 5.7 | 12.766 | 5.7 | 15.3191 | 5.7 | 17.8723 | 5.7 | 20.4255 | 5.7 | 22.9787 | 5.7 | 25.5319
5.8 | 1.25 | 5.8 | 2.5 | 5.8 | 5 | 5.8 | 7.5 | 5.8 | 10 | 5.8 | 12.5 | 5.8 | 15 | 5.8 | 17.5 | 5.8 | 20 | 5.8 | 22.5 | 5.8 | 25
5.9 | 1.2245 | 5.9 | 2.449 | 5.9 | 4.898 | 5.9 | 7.3469 | 5.9 | 9.7959 | 5.9 | 12.2449 | 5.9 | 14.6939 | 5.9 | 17.1429 | 5.9 | 19.5918 | 5.9 | 22.0408 | 5.9 | 24.4898
6 | 1.2 | 6 | 2.4 | 6 | 4.8 | 6 | 7.2 | 6 | 9.6 | 6 | 12 | 6 | 14.4 | 6 | 16.8 | 6 | 19.2 | 6 | 21.6 | 6 | 24
6.1 | 1.1765 | 6.1 | 2.3529 | 6.1 | 4.7059 | 6.1 | 7.0588 | 6.1 | 9.4118 | 6.1 | 11.7647 | 6.1 | 14.1176 | 6.1 | 16.4706 | 6.1 | 18.8235 | 6.1 | 21.1765 | 6.1 | 23.5294
6.2 | 1.1538 | 6.2 | 2.3077 | 6.2 | 4.6154 | 6.2 | 6.9231 | 6.2 | 9.2308 | 6.2 | 11.5385 | 6.2 | 13.8462 | 6.2 | 16.1538 | 6.2 | 18.4615 | 6.2 | 20.7692 | 6.2 | 23.0769
6.3 | 1.1321 | 6.3 | 2.2642 | 6.3 | 4.5283 | 6.3 | 6.7925 | 6.3 | 9.0566 | 6.3 | 11.3208 | 6.3 | 13.5849 | 6.3 | 15.8491 | 6.3 | 18.1132 | 6.3 | 20.3774 | 6.3 | 22.6415
6.4 | 1.1111 | 6.4 | 2.2222 | 6.4 | 4.4444 | 6.4 | 6.6667 | 6.4 | 8.8889 | 6.4 | 11.1111 | 6.4 | 13.3333 | 6.4 | 15.5556 | 6.4 | 17.7778 | 6.4 | 20 | 6.4 | 22.2222
6.5 | 1.0909 | 6.5 | 2.1818 | 6.5 | 4.3636 | 6.5 | 6.5455 | 6.5 | 8.7273 | 6.5 | 10.9091 | 6.5 | 13.0909 | 6.5 | 15.2727 | 6.5 | 17.4545 | 6.5 | 19.6364 | 6.5 | 21.8182
6.6 | 1.0714 | 6.6 | 2.1429 | 6.6 | 4.2857 | 6.6 | 6.4286 | 6.6 | 8.5714 | 6.6 | 10.7143 | 6.6 | 12.8571 | 6.6 | 15 | 6.6 | 17.1429 | 6.6 | 19.2857 | 6.6 | 21.4286
6.7 | 1.0526 | 6.7 | 2.1053 | 6.7 | 4.2105 | 6.7 | 6.3158 | 6.7 | 8.4211 | 6.7 | 10.5263 | 6.7 | 12.6316 | 6.7 | 14.7368 | 6.7 | 16.8421 | 6.7 | 18.9474 | 6.7 | 21.0526
6.8 | 1.0345 | 6.8 | 2.069 | 6.8 | 4.1379 | 6.8 | 6.2069 | 6.8 | 8.2759 | 6.8 | 10.3448 | 6.8 | 12.4138 | 6.8 | 14.4828 | 6.8 | 16.5517 | 6.8 | 18.6207 | 6.8 | 20.6897
6.9 | 1.0169 | 6.9 | 2.0339 | 6.9 | 4.0678 | 6.9 | 6.1017 | 6.9 | 8.1356 | 6.9 | 10.1695 | 6.9 | 12.2034 | 6.9 | 14.2373 | 6.9 | 16.2712 | 6.9 | 18.3051 | 6.9 | 20.339
7 | 1 | 7 | 2 | 7 | 4 | 7 | 6 | 7 | 8 | 7 | 10 | 7 | 12 | 7 | 14 | 7 | 16 | 7 | 18 | 7 | 20
7.1 | 0.98361 | 7.1 | 1.9672 | 7.1 | 3.9344 | 7.1 | 5.9016 | 7.1 | 7.8689 | 7.1 | 9.8361 | 7.1 | 11.8033 | 7.1 | 13.7705 | 7.1 | 15.7377 | 7.1 | 17.7049 | 7.1 | 19.6721
7.2 | 0.96774 | 7.2 | 1.9355 | 7.2 | 3.871 | 7.2 | 5.8065 | 7.2 | 7.7419 | 7.2 | 9.6774 | 7.2 | 11.6129 | 7.2 | 13.5484 | 7.2 | 15.4839 | 7.2 | 17.4194 | 7.2 | 19.3548
7.3 | 0.95238 | 7.3 | 1.9048 | 7.3 | 3.8095 | 7.3 | 5.7143 | 7.3 | 7.619 | 7.3 | 9.5238 | 7.3 | 11.4286 | 7.3 | 13.3333 | 7.3 | 15.2381 | 7.3 | 17.1429 | 7.3 | 19.0476
7.4 | 0.9375 | 7.4 | 1.875 | 7.4 | 3.75 | 7.4 | 5.625 | 7.4 | 7.5 | 7.4 | 9.375 | 7.4 | 11.25 | 7.4 | 13.125 | 7.4 | 15 | 7.4 | 16.875 | 7.4 | 18.75
7.5 | 0.92308 | 7.5 | 1.8462 | 7.5 | 3.6923 | 7.5 | 5.5385 | 7.5 | 7.3846 | 7.5 | 9.2308 | 7.5 | 11.0769 | 7.5 | 12.9231 | 7.5 | 14.7692 | 7.5 | 16.6154 | 7.5 | 18.4615
7.6 | 0.90909 | 7.6 | 1.8182 | 7.6 | 3.6364 | 7.6 | 5.4545 | 7.6 | 7.2727 | 7.6 | 9.0909 | 7.6 | 10.9091 | 7.6 | 12.7273 | 7.6 | 14.5455 | 7.6 | 16.3636 | 7.6 | 18.1818
7.7 | 0.89552 | 7.7 | 1.791 | 7.7 | 3.5821 | 7.7 | 5.3731 | 7.7 | 7.1642 | 7.7 | 8.9552 | 7.7 | 10.7463 | 7.7 | 12.5373 | 7.7 | 14.3284 | 7.7 | 16.1194 | 7.7 | 17.9104
7.8 | 0.88235 | 7.8 | 1.7647 | 7.8 | 3.5294 | 7.8 | 5.2941 | 7.8 | 7.0588 | 7.8 | 8.8235 | 7.8 | 10.5882 | 7.8 | 12.3529 | 7.8 | 14.1176 | 7.8 | 15.8824 | 7.8 | 17.6471
7.9 | 0.86957 | 7.9 | 1.7391 | 7.9 | 3.4783 | 7.9 | 5.2174 | 7.9 | 6.9565 | 7.9 | 8.6957 | 7.9 | 10.4348 | 7.9 | 12.1739 | 7.9 | 13.913 | 7.9 | 15.6522 | 7.9 | 17.3913
8 | 0.85714 | 8 | 1.7143 | 8 | 3.4286 | 8 | 5.1429 | 8 | 6.8571 | 8 | 8.5714 | 8 | 10.2857 | 8 | 12 | 8 | 13.7143 | 8 | 15.4286 | 8 | 17.1429
8.1 | 0.84507 | 8.1 | 1.6901 | 8.1 | 3.3803 | 8.1 | 5.0704 | 8.1 | 6.7606 | 8.1 | 8.4507 | 8.1 | 10.1408 | 8.1 | 11.831 | 8.1 | 13.5211 | 8.1 | 15.2113 | 8.1 | 16.9014
8.2 | 0.83333 | 8.2 | 1.6667 | 8.2 | 3.3333 | 8.2 | 5 | 8.2 | 6.6667 | 8.2 | 8.3333 | 8.2 | 10 | 8.2 | 11.6667 | 8.2 | 13.3333 | 8.2 | 15 | 8.2 | 16.6667
8.3 | 0.82192 | 8.3 | 1.6438 | 8.3 | 3.2877 | 8.3 | 4.9315 | 8.3 | 6.5753 | 8.3 | 8.2192 | 8.3 | 9.863 | 8.3 | 11.5068 | 8.3 | 13.1507 | 8.3 | 14.7945 | 8.3 | 16.4384
8.4 | 0.81081 | 8.4 | 1.6216 | 8.4 | 3.2432 | 8.4 | 4.8649 | 8.4 | 6.4865 | 8.4 | 8.1081 | 8.4 | 9.7297 | 8.4 | 11.3514 | 8.4 | 12.973 | 8.4 | 14.5946 | 8.4 | 16.2162
8.5 | 0.8 | 8.5 | 1.6 | 8.5 | 3.2 | 8.5 | 4.8 | 8.5 | 6.4 | 8.5 | 8 | 8.5 | 9.6 | 8.5 | 11.2 | 8.5 | 12.8 | 8.5 | 14.4 | 8.5 | 16
8.6 | 0.78947 | 8.6 | 1.5789 | 8.6 | 3.1579 | 8.6 | 4.7368 | 8.6 | 6.3158 | 8.6 | 7.8947 | 8.6 | 9.4737 | 8.6 | 11.0526 | 8.6 | 12.6316 | 8.6 | 14.2105 | 8.6 | 15.7895
8.7 | 0.77922 | 8.7 | 1.5584 | 8.7 | 3.1169 | 8.7 | 4.6753 | 8.7 | 6.2338 | 8.7 | 7.7922 | 8.7 | 9.3506 | 8.7 | 10.9091 | 8.7 | 12.4675 | 8.7 | 14.026 | 8.7 | 15.5844
8.8 | 0.76923 | 8.8 | 1.5385 | 8.8 | 3.0769 | 8.8 | 4.6154 | 8.8 | 6.1538 | 8.8 | 7.6923 | 8.8 | 9.2308 | 8.8 | 10.7692 | 8.8 | 12.3077 | 8.8 | 13.8462 | 8.8 | 15.3846
8.9 | 0.75949 | 8.9 | 1.519 | 8.9 | 3.038 | 8.9 | 4.557 | 8.9 | 6.0759 | 8.9 | 7.5949 | 8.9 | 9.1139 | 8.9 | 10.6329 | 8.9 | 12.1519 | 8.9 | 13.6709 | 8.9 | 15.1899
9 | 0.75 | 9 | 1.5 | 9 | 3 | 9 | 4.5 | 9 | 6 | 9 | 7.5 | 9 | 9 | 9 | 10.5 | 9 | 12 | 9 | 13.5 | 9 | 15
9.1 | 0.74074 | 9.1 | 1.4815 | 9.1 | 2.963 | 9.1 | 4.4444 | 9.1 | 5.9259 | 9.1 | 7.4074 | 9.1 | 8.8889 | 9.1 | 10.3704 | 9.1 | 11.8519 | 9.1 | 13.3333 | 9.1 | 14.8148
9.2 | 0.73171 | 9.2 | 1.4634 | 9.2 | 2.9268 | 9.2 | 4.3902 | 9.2 | 5.8537 | 9.2 | 7.3171 | 9.2 | 8.7805 | 9.2 | 10.2439 | 9.2 | 11.7073 | 9.2 | 13.1707 | 9.2 | 14.6341
9.3 | 0.72289 | 9.3 | 1.4458 | 9.3 | 2.8916 | 9.3 | 4.3373 | 9.3 | 5.7831 | 9.3 | 7.2289 | 9.3 | 8.6747 | 9.3 | 10.1205 | 9.3 | 11.5663 | 9.3 | 13.012 | 9.3 | 14.4578
9.4 | 0.71429 | 9.4 | 1.4286 | 9.4 | 2.8571 | 9.4 | 4.2857 | 9.4 | 5.7143 | 9.4 | 7.1429 | 9.4 | 8.5714 | 9.4 | 10 | 9.4 | 11.4286 | 9.4 | 12.8571 | 9.4 | 14.2857
9.5 | 0.70588 | 9.5 | 1.4118 | 9.5 | 2.8235 | 9.5 | 4.2353 | 9.5 | 5.6471 | 9.5 | 7.0588 | 9.5 | 8.4706 | 9.5 | 9.8824 | 9.5 | 11.2941 | 9.5 | 12.7059 | 9.5 | 14.1176
9.6 | 0.69767 | 9.6 | 1.3953 | 9.6 | 2.7907 | 9.6 | 4.186 | 9.6 | 5.5814 | 9.6 | 6.9767 | 9.6 | 8.3721 | 9.6 | 9.7674 | 9.6 | 11.1628 | 9.6 | 12.5581 | 9.6 | 13.9535
9.7 | 0.68966 | 9.7 | 1.3793 | 9.7 | 2.7586 | 9.7 | 4.1379 | 9.7 | 5.5172 | 9.7 | 6.8966 | 9.7 | 8.2759 | 9.7 | 9.6552 | 9.7 | 11.0345 | 9.7 | 12.4138 | 9.7 | 13.7931
9.8 | 0.68182 | 9.8 | 1.3636 | 9.8 | 2.7273 | 9.8 | 4.0909 | 9.8 | 5.4545 | 9.8 | 6.8182 | 9.8 | 8.1818 | 9.8 | 9.5455 | 9.8 | 10.9091 | 9.8 | 12.2727 | 9.8 | 13.6364
9.9 | 0.67416 | 9.9 | 1.3483 | 9.9 | 2.6966 | 9.9 | 4.0449 | 9.9 | 5.3933 | 9.9 | 6.7416 | 9.9 | 8.0899 | 9.9 | 9.4382 | 9.9 | 10.7865 | 9.9 | 12.1348 | 9.9 | 13.4831
10 | 0.66667 | 10 | 1.3333 | 10 | 2.6667 | 10 | 4 | 10 | 5.3333 | 10 | 6.6667 | 10 | 8 | 10 | 9.3333 | 10 | 10.6667 | 10 | 12 | 10 | 13.3333
10.5 | 0.63158 | 10.5 | 1.2632 | 10.5 | 2.5263 | 10.5 | 3.7895 | 10.5 | 5.0526 | 10.5 | 6.3158 | 10.5 | 7.5789 | 10.5 | 8.8421 | 10.5 | 10.1053 | 10.5 | 11.3684 | 10.5 | 12.6316
11 | 0.6 | 11 | 1.2 | 11 | 2.4 | 11 | 3.6 | 11 | 4.8 | 11 | 6 | 11 | 7.2 | 11 | 8.4 | 11 | 9.6 | 11 | 10.8 | 11 | 12
11.5 | 0.57143 | 11.5 | 1.1429 | 11.5 | 2.2857 | 11.5 | 3.4286 | 11.5 | 4.5714 | 11.5 | 5.7143 | 11.5 | 6.8571 | 11.5 | 8 | 11.5 | 9.1429 | 11.5 | 10.2857 | 11.5 | 11.4286
12 | 0.54545 | 12 | 1.0909 | 12 | 2.1818 | 12 | 3.2727 | 12 | 4.3636 | 12 | 5.4545 | 12 | 6.5455 | 12 | 7.6364 | 12 | 8.7273 | 12 | 9.8182 | 12 | 10.9091
12.5 | 0.52174 | 12.5 | 1.0435 | 12.5 | 2.087 | 12.5 | 3.1304 | 12.5 | 4.1739 | 12.5 | 5.2174 | 12.5 | 6.2609 | 12.5 | 7.3043 | 12.5 | 8.3478 | 12.5 | 9.3913 | 12.5 | 10.4348
13 | 0.5 | 13 | 1 | 13 | 2 | 13 | 3 | 13 | 4 | 13 | 5 | 13 | 6 | 13 | 7 | 13 | 8 | 13 | 9 | 13 | 10
13.5 | 0.48 | 13.5 | 0.96 | 13.5 | 1.92 | 13.5 | 2.88 | 13.5 | 3.84 | 13.5 | 4.8 | 13.5 | 5.76 | 13.5 | 6.72 | 13.5 | 7.68 | 13.5 | 8.64 | 13.5 | 9.6
14 | 0.46154 | 14 | 0.92308 | 14 | 1.8462 | 14 | 2.7692 | 14 | 3.6923 | 14 | 4.6154 | 14 | 5.5385 | 14 | 6.4615 | 14 | 7.3846 | 14 | 8.3077 | 14 | 9.2308
14.5 | 0.44444 | 14.5 | 0.88889 | 14.5 | 1.7778 | 14.5 | 2.6667 | 14.5 | 3.5556 | 14.5 | 4.4444 | 14.5 | 5.3333 | 14.5 | 6.2222 | 14.5 | 7.1111 | 14.5 | 8 | 14.5 | 8.8889
15 | 0.42857 | 15 | 0.85714 | 15 | 1.7143 | 15 | 2.5714 | 15 | 3.4286 | 15 | 4.2857 | 15 | 5.1429 | 15 | 6 | 15 | 6.8571 | 15 | 7.7143 | 15 | 8.5714
16 | 0.4 | 16 | 0.8 | 16 | 1.6 | 16 | 2.4 | 16 | 3.2 | 16 | 4 | 16 | 4.8 | 16 | 5.6 | 16 | 6.4 | 16 | 7.2 | 16 | 8
17 | 0.375 | 17 | 0.75 | 17 | 1.5 | 17 | 2.25 | 17 | 3 | 17 | 3.75 | 17 | 4.5 | 17 | 5.25 | 17 | 6 | 17 | 6.75 | 17 | 7.5
18 | 0.35294 | 18 | 0.70588 | 18 | 1.4118 | 18 | 2.1176 | 18 | 2.8235 | 18 | 3.5294 | 18 | 4.2353 | 18 | 4.9412 | 18 | 5.6471 | 18 | 6.3529 | 18 | 7.0588
19 | 0.33333 | 19 | 0.66667 | 19 | 1.3333 | 19 | 2 | 19 | 2.6667 | 19 | 3.3333 | 19 | 4 | 19 | 4.6667 | 19 | 5.3333 | 19 | 6 | 19 | 6.6667
20 | 0.31579 | 20 | 0.63158 | 20 | 1.2632 | 20 | 1.8947 | 20 | 2.5263 | 20 | 3.1579 | 20 | 3.7895 | 20 | 4.4211 | 20 | 5.0526 | 20 | 5.6842 | 20 | 6.3158
21 | 0.3 | 21 | 0.6 | 21 | 1.2 | 21 | 1.8 | 21 | 2.4 | 21 | 3 | 21 | 3.6 | 21 | 4.2 | 21 | 4.8 | 21 | 5.4 | 21 | 6
22 | 0.28571 | 22 | 0.57143 | 22 | 1.1429 | 22 | 1.7143 | 22 | 2.2857 | 22 | 2.8571 | 22 | 3.4286 | 22 | 4 | 22 | 4.5714 | 22 | 5.1429 | 22 | 5.7143
23 | 0.27273 | 23 | 0.54545 | 23 | 1.0909 | 23 | 1.6364 | 23 | 2.1818 | 23 | 2.7273 | 23 | 3.2727 | 23 | 3.8182 | 23 | 4.3636 | 23 | 4.9091 | 23 | 5.4545
24 | 0.26087 | 24 | 0.52174 | 24 | 1.0435 | 24 | 1.5652 | 24 | 2.087 | 24 | 2.6087 | 24 | 3.1304 | 24 | 3.6522 | 24 | 4.1739 | 24 | 4.6957 | 24 | 5.2174
25 | 0.25 | 25 | 0.5 | 25 | 1 | 25 | 1.5 | 25 | 2 | 25 | 2.5 | 25 | 3 | 25 | 3.5 | 25 | 4 | 25 | 4.5 | 25 | 5
26 | 0.24 | 26 | 0.48 | 26 | 0.96 | 26 | 1.44 | 26 | 1.92 | 26 | 2.4 | 26 | 2.88 | 26 | 3.36 | 26 | 3.84 | 26 | 4.32 | 26 | 4.8
27 | 0.23077 | 27 | 0.46154 | 27 | 0.92308 | 27 | 1.3846 | 27 | 1.8462 | 27 | 2.3077 | 27 | 2.7692 | 27 | 3.2308 | 27 | 3.6923 | 27 | 4.1538 | 27 | 4.6154
28 | 0.22222 | 28 | 0.44444 | 28 | 0.88889 | 28 | 1.3333 | 28 | 1.7778 | 28 | 2.2222 | 28 | 2.6667 | 28 | 3.1111 | 28 | 3.5556 | 28 | 4 | 28 | 4.4444
29 | 0.21429 | 29 | 0.42857 | 29 | 0.85714 | 29 | 1.2857 | 29 | 1.7143 | 29 | 2.1429 | 29 | 2.5714 | 29 | 3 | 29 | 3.4286 | 29 | 3.8571 | 29 | 4.2857
30 | 0.2069 | 30 | 0.41379 | 30 | 0.82759 | 30 | 1.2414 | 30 | 1.6552 | 30 | 2.069 | 30 | 2.4828 | 30 | 2.8966 | 30 | 3.3103 | 30 | 3.7241 | 30 | 4.1379
31 | 0.2069 | 31 | 0.41379 | 31 | 0.82759 | 31 | 1.2414 | 31 | 1.6552 | 31 | 2.069 | 31 | 2.4828 | 31 | 2.8966 | 31 | 3.3103 | 31 | 3.7241 | 31 | 4.1379
32 | 0.2069 | 32 | 0.41379 | 32 | 0.82759 | 32 | 1.2414 | 32 | 1.6552 | 32 | 2.069 | 32 | 2.4828 | 32 | 2.8966 | 32 | 3.3103 | 32 | 3.7241 | 32 | 4.1379
33 | 0.2069 | 33 | 0.41379 | 33 | 0.82759 | 33 | 1.2414 | 33 | 1.6552 | 33 | 2.069 | 33 | 2.4828 | 33 | 2.8966 | 33 | 3.3103 | 33 | 3.7241 | 33 | 4.1379
34 | 0.2069 | 34 | 0.41379 | 34 | 0.82759 | 34 | 1.2414 | 34 | 1.6552 | 34 | 2.069 | 34 | 2.4828 | 34 | 2.8966 | 34 | 3.3103 | 34 | 3.7241 | 34 | 4.1379
35 | 0.2069 | 35 | 0.41379 | 35 | 0.82759 | 35 | 1.2414 | 35 | 1.6552 | 35 | 2.069 | 35 | 2.4828 | 35 | 2.8966 | 35 | 3.3103 | 35 | 3.7241 | 35 | 4.1379
36 | 0.2069 | 36 | 0.41379 | 36 | 0.82759 | 36 | 1.2414 | 36 | 1.6552 | 36 | 2.069 | 36 | 2.4828 | 36 | 2.8966 | 36 | 3.3103 | 36 | 3.7241 | 36 | 4.1379
37 | 0.2069 | 37 | 0.41379 | 37 | 0.82759 | 37 | 1.2414 | 37 | 1.6552 | 37 | 2.069 | 37 | 2.4828 | 37 | 2.8966 | 37 | 3.3103 | 37 | 3.7241 | 37 | 4.1379
38 | 0.2069 | 38 | 0.41379 | 38 | 0.82759 | 38 | 1.2414 | 38 | 1.6552 | 38 | 2.069 | 38 | 2.4828 | 38 | 2.8966 | 38 | 3.3103 | 38 | 3.7241 | 38 | 4.1379
39 | 0.2069 | 39 | 0.41379 | 39 | 0.82759 | 39 | 1.2414 | 39 | 1.6552 | 39 | 2.069 | 39 | 2.4828 | 39 | 2.8966 | 39 | 3.3103 | 39 | 3.7241 | 39 | 4.1379
40 | 0.2069 | 40 | 0.41379 | 40 | 0.82759 | 40 | 1.2414 | 40 | 1.6552 | 40 | 2.069 | 40 | 2.4828 | 40 | 2.8966 | 40 | 3.3103 | 40 | 3.7241 | 40 | 4.1379
41 | 0.2069 | 41 | 0.41379 | 41 | 0.82759 | 41 | 1.2414 | 41 | 1.6552 | 41 | 2.069 | 41 | 2.4828 | 41 | 2.8966 | 41 | 3.3103 | 41 | 3.7241 | 41 | 4.1379
42 | 0.2069 | 42 | 0.41379 | 42 | 0.82759 | 42 | 1.2414 | 42 | 1.6552 | 42 | 2.069 | 42 | 2.4828 | 42 | 2.8966 | 42 | 3.3103 | 42 | 3.7241 | 42 | 4.1379
43 | 0.2069 | 43 | 0.41379 | 43 | 0.82759 | 43 | 1.2414 | 43 | 1.6552 | 43 | 2.069 | 43 | 2.4828 | 43 | 2.8966 | 43 | 3.3103 | 43 | 3.7241 | 43 | 4.1379
44 | 0.2069 | 44 | 0.41379 | 44 | 0.82759 | 44 | 1.2414 | 44 | 1.6552 | 44 | 2.069 | 44 | 2.4828 | 44 | 2.8966 | 44 | 3.3103 | 44 | 3.7241 | 44 | 4.1379
45 | 0.2069 | 45 | 0.41379 | 45 | 0.82759 | 45 | 1.2414 | 45 | 1.6552 | 45 | 2.069 | 45 | 2.4828 | 45 | 2.8966 | 45 | 3.3103 | 45 | 3.7241 | 45 | 4.1379
46 | 0.2069 | 46 | 0.41379 | 46 | 0.82759 | 46 | 1.2414 | 46 | 1.6552 | 46 | 2.069 | 46 | 2.4828 | 46 | 2.8966 | 46 | 3.3103 | 46 | 3.7241 | 46 | 4.1379
47 | 0.2069 | 47 | 0.41379 | 47 | 0.82759 | 47 | 1.2414 | 47 | 1.6552 | 47 | 2.069 | 47 | 2.4828 | 47 | 2.8966 | 47 | 3.3103 | 47 | 3.7241 | 47 | 4.1379
48 | 0.2069 | 48 | 0.41379 | 48 | 0.82759 | 48 | 1.2414 | 48 | 1.6552 | 48 | 2.069 | 48 | 2.4828 | 48 | 2.8966 | 48 | 3.3103 | 48 | 3.7241 | 48 | 4.1379
49 | 0.2069 | 49 | 0.41379 | 49 | 0.82759 | 49 | 1.2414 | 49 | 1.6552 | 49 | 2.069 | 49 | 2.4828 | 49 | 2.8966 | 49 | 3.3103 | 49 | 3.7241 | 49 | 4.1379
50 | 0.2069 | 50 | 0.41379 | 50 | 0.82759 | 50 | 1.2414 | 50 | 1.6552 | 50 | 2.069 | 50 | 2.4828 | 50 | 2.8966 | 50 | 3.3103 | 50 | 3.7241 | 50 | 4.1379
55 | 0.2069 | 55 | 0.41379 | 55 | 0.82759 | 55 | 1.2414 | 55 | 1.6552 | 55 | 2.069 | 55 | 2.4828 | 55 | 2.8966 | 55 | 3.3103 | 55 | 3.7241 | 55 | 4.1379
60 | 0.2069 | 60 | 0.41379 | 60 | 0.82759 | 60 | 1.2414 | 60 | 1.6552 | 60 | 2.069 | 60 | 2.4828 | 60 | 2.8966 | 60 | 3.3103 | 60 | 3.7241 | 60 | 4.1379
65 | 0.2069 | 65 | 0.41379 | 65 | 0.82759 | 65 | 1.2414 | 65 | 1.6552 | 65 | 2.069 | 65 | 2.4828 | 65 | 2.8966 | 65 | 3.3103 | 65 | 3.7241 | 65 | 4.1379
70 | 0.2069 | 70 | 0.41379 | 70 | 0.82759 | 70 | 1.2414 | 70 | 1.6552 | 70 | 2.069 | 70 | 2.4828 | 70 | 2.8966 | 70 | 3.3103 | 70 | 3.7241 | 70 | 4.1379
75 | 0.2069 | 75 | 0.41379 | 75 | 0.82759 | 75 | 1.2414 | 75 | 1.6552 | 75 | 2.069 | 75 | 2.4828 | 75 | 2.8966 | 75 | 3.3103 | 75 | 3.7241 | 75 | 4.1379
80 | 0.2069 | 80 | 0.41379 | 80 | 0.82759 | 80 | 1.2414 | 80 | 1.6552 | 80 | 2.069 | 80 | 2.4828 | 80 | 2.8966 | 80 | 3.3103 | 80 | 3.7241 | 80 | 4.1379
85 | 0.2069 | 85 | 0.41379 | 85 | 0.82759 | 85 | 1.2414 | 85 | 1.6552 | 85 | 2.069 | 85 | 2.4828 | 85 | 2.8966 | 85 | 3.3103 | 85 | 3.7241 | 85 | 4.1379
90 | 0.2069 | 90 | 0.41379 | 90 | 0.82759 | 90 | 1.2414 | 90 | 1.6552 | 90 | 2.069 | 90 | 2.4828 | 90 | 2.8966 | 90 | 3.3103 | 90 | 3.7241 | 90 | 4.1379
95 | 0.2069 | 95 | 0.41379 | 95 | 0.82759 | 95 | 1.2414 | 95 | 1.6552 | 95 | 2.069 | 95 | 2.4828 | 95 | 2.8966 | 95 | 3.3103 | 95 | 3.7241 | 95 | 4.1379
100 | 0.2069 | 100 | 0.41379 | 100 | 0.82759 | 100 | 1.2414 | 100 | 1.6552 | 100 | 2.069 | 100 | 2.4828 | 100 | 2.8966 | 100 | 3.3103 | 100 | 3.7241 | 100 | 4.1379